ENG14-3.1.2.6

Input paper for the following Committee(s): 	check as appropriate		Purpose of paper:

□ARM	XENG		□PAP					X  Input

□ENAV	□VTS							□  Information

Agenda item

Technical Domain / Task Number 2	…ENG 2.4.1……………………

Author(s) / Submitter(s)			……China MSA……………

Solar charge controller

# Summary

The application of AtoN solar panels in China is mature, and China has a complete industrial chain of solar panel equipment. According to the application of AtoN solar panel in China, this paper introduces a AtoN solar panel charge controller, which provides opinions for the ENG committee to formulate the AtoN solar panel guidelines.

## Purpose of proposal

The committee is requested to consider this proposal and take appropriate action .

## Related documents

- G1039-1 《IALA solar powers system calculation tool》

- G1039 -2《handbook for meterological data for IALA solar power system calculation tool》

- G1039 《desiging solar power systemm for aids to navigation》

- G1067-0 《selection of power systems for AtoN and associated Equipment》

- G1067-1 《Total Electrical Loads of AtoN》

- G1067-2 《Power Sources》

- G1067-3《Electrical Energy Storage for AtoN》

# Background

## 2.1   Advantages of solar charging system

Coastal AtoN are generally located on islands, reefs or water far away from land, so it usually difficult to connect to local main supply. In the southern coastal area of Guangdong, China, the annual sunshine is about 2200-3000 hours, it can annually produce about (586-796) * 104kj / m2 of solar energy, which is equivalent to the energy generated by the combustion of 200-225kg standard coal. Solar power supply has the advantages of strong reliability, easy installation, long service life, environmental friendly and wide application. It has become one of the main power supply for coastal navigation aids. Solar power supply also has the following advantages:

(1) Less moving parts;

(2) Less maintenance requirements except cleaning;

(3) Less attenuation of output power in the life cycle;

(4) No need to connect to local main supply, and the manual maintenance cost is low;

(5) The charging process is separated from the working process of the lantern (the solar panel charges the battery during the day and the battery supplies power to the lamp at night), so as to optimize t

he battery charging and discharging process and will not affect the working life of the battery and lantern.

At present, the solar power supply system for AtoN is widely used, as shown in the figure below:

Load

Battery

Solar panels

Figure.1  solar power supply system for Aton

## 2.2   Disadvantages of independent solar charging system

The charge effectiveness of the solar module is affected by sunlight, it is easy to charge the battery to upper voltage limit because of the intense and long sunshine in summer. If the solar module continues to charge the battery after the battery is fully charged , most of the electrical energy delivered by the solar module will be converted into thermal energy,  which can cause battery temperature increases, internal pressure increases, and after reaching a certain pressure, some battery damage like electrolyte decreases, battery sulfation, battery capacity decreases occurs. And, in winter or continuous cloudy weather, there is short and inefficient sunlight, the battery's energy consumed at night and cannot be replenished in time, and after some time the battery capacity maybe decrease rapidly.

# solar charge controller

In order to avoid the said problem, the solar charge controller can be use to regulate and control the charging and discharging conditions of the battery, and control the electric energy output of the solar panel, meanwhile control the battery output according to the power demand of the load.

## 3.1    block diagram and principle of solar charge controller system

Solar panel papanpapanels

Solar charge controller

Remote and control unit

Battery

load

Figure 2:  solar charging system with controller

The Aton solar power system mainly consists of the solar panel,solar charge controller, battery, load, and the data transfer unit. The solar panel charges battery through the solar charge controller, which provides overdischarge and overcurrent protection for the battery. At the same time, the solar charge controller can also be connected to a remote and control unit , with which the working parameters of the system can be transmitted back to the data center, so as to realize the monitoring of the working status of the entire energy system.

## 3.2    A solar charge controller

Solar panel input

Load interface

Model switch

Software upgrade

Battery output

LED display

Battery input

Data exchange

Figure 3:A solar charge controller

Figure (3) shows a real solar charge controller produced by Chengdu Dixin Technology Co., Ltd. It is mainly composed of power module, main control chip, buttons, display, data exchange module, solar charging overvoltage and overcurrent detection control module, battery discharge detection control module and ADC acquisition module. The solar charge controller mainly realizes the following functions:

- 1.  Charging overcurrent protection: When charging current is over limited value, the controller will generate a cycle protection once a second until the current back to limited value.

- 2.  Charging overvoltage protection: When charging voltage is over limited value, the controller will generate a cycle protection once a second until the voltage back to limited value.

- 3.   Automatically compatible with batteries: The solar charge controller is automatically compatible with 12V/24V batteries, the upper voltage limited value for 12V charging is 14.4±0.2V, and the upper voltage limited value for 24V charging is 28.8±0.2V.

- 4.   Short-circuit protection: When a solar input short-circuit occurs, the solar controller generates a cycle protection once a second and displays the corresponding fault code until the fault is processed.

- 5.   Battery discharge overcurrent protection: When the battery discharge current is over limited value, the solar controller first generates a 100ms delay. After the delay is completed, it will not generate protection if it doesn`t detects overcurrent, otherwise it will generate overcurrent protection. By which it can enable the controller to access inductive loads and large capacity loads. After the protection is generated, it will delay 900ms to restore the unprotected state. If it is still overcurrent, the controller continue to circulate the above protection and display the corresponding fault code until the fault is processed.

- 6.   Voltage and current acquisition and display: The voltage and current are collected through the internal 10-bit ADC of the main control chip. The solar voltage, current, and battery voltage are collected 10 times and averaged, and the time interval between the two collections is 50ms. The load current is continuously collected for 35 seconds and the collection period is 1ms. This design enables the solar charge controller to capture the flashing light current of the Aton lamp. And the collected lamp current can be saved to the next collection cycle, and the lamp current data will not be cleared until the next cycle is completed and the lamp current is not collected.

- 7.    Detected data collection: The solar controller has data collecting module, and the main control chip communicates with the wireless device through the data collecting module, and sends the detected voltage and current data to the control center.

- 8.    Program upgrade: The solar controller can upgrade the program at any time and change the relevant working parameters of the controller to adapt to different application scenarios.

# Proposal

Because the charging voltage and current of the solar panel are affected by the sunlight, and the sunlight intensity and duration is vary from time to time in the same place, which leads to the unstable charging state of the solar panel, and easily lead to battery overload or overdischarge. From our experience in the South China Sea, the AtoN battery is prone to overcharge in summer and overdischarge in winter or rainy season,which can significantly shorten the service life of the AtoN battery or cause light extinguish.

In summary, the application of solar charge controller has practically positive significance for the AtoN energy system.It is proposed that the solar panel guidelines work group should add some content about solar charge controller in the new guidelines, as attached draft of the guidelines submitted by China MSA.

# Action requested of the committee

The committee is requested to consider the information provide above and add some content to the new solar panel guideline in Section 7.3 “the impact of regulation”, shown as attached draft submit by China MSA.

# ANNEX. Draft wording for section 7.3“the impact of regulation”.

# ANNEX. Draft wording for section 7.3“the impact of regulation”

## Impact of solar regulation

The charge effectiveness of the solar module is affected by sunlight, it is easy to charge the battery to upper voltage limit because of the intense and long sunshine in summer. If the solar module continues to charge the battery after the battery is fully charged , most of the electrical energy delivered by the solar module will be converted into thermal energy,  which can cause battery temperature increases, internal pressure increases and so on,  some battery damage like electrolyte decreases, battery sulfation, battery capacity decreases occurs. And, in winter or continuous cloudy weather, there is short and inefficient sunlight, the battery's energy consumed at night and cannot be replenished in time, and after some time the battery capacity may decrease rapidly.The application of the regulator can effectively prevent the solar battery from overcharging, and some regulator can also protect the battery from overdischarging when the solar module is insufficient. However, it should be noted that the regulator itself does not provide energy and cannot solve the problem of insufficient battery capacity. This problem can be solved by other methods, such as increasing the capacity of the solar module or battery.

### 7.3.1   charge controller

- Solar charging system with controller

- A solar charge controller

Solar charge controller is a adoptable device for AtoN solar panel system, which can regulate the charging and discharging conditions of the battery, and control the power output  according to the demand of load,  protects batteries and related loads. At the same time, some charge controller can also be connected to a telemetry remote control terminal to monitor the working status of the AtoN energy system. However, whether it is necessary to use solar controller should be overall considered according to  the actual situation including the additional purchasing or maintenance cost. And some battery or integrated lantern contains charging or discharging protection element , which means there is no need to use solar charge controller at all.

Refer to G1067‐1 《Total electrical load of AtoN 》section 5.9 “charge controller”.

Leave open if uncertain