IALA Guideline

G1???

Properties of a good marine solar Module

Edition 1.0

Document date

Revisions to this IALA Document are to be noted in the table prior to the issue of a revised document.

| Date | Page / Section Revised | Requirement for Revision |
| --- | --- | --- |
| Mar 21 | All | New guideline |

1	Introduction	7

2	Scope	7

3	THE Use of solar panels as power source for aton	7

3.1	How to recognize the best photovoltaic panels on the market?	8

4	Technology	8

4.1	Monocrystalline	8

4.2	Polycrystalline	8

4.3	Thin film / flexible modules	8

4.4	Monocrystalline vs Polycrystalline panels	9

5	Design	9

5.1	Number of cells	10

5.2	Intercell connection	10

5.3	Colour	11

5.4	Shock and vibration	12

5.5	Module efficiency	12

5.6	Diodes	13

5.7	Construction of modules	14

5.7.1	Glazing material	14

5.7.2	Backing material	15

5.8	Quality	15

5.9	Ingress protection	15

5.10	Humidity and condensation	16

5.11	Wind loading	16

5.12	Electrical Performance	17

5.13	Operating conditions – Part of environmental factors?	17

6	Environmental factors	17

6.1	Materials used in production	18

6.2	Deposits	18

6.2.1	Bird Foul (Guano)	18

6.2.2	Salt	19

6.2.3	Dust	19

7	Temperature	19

7.1	Humidity	20

7.2	Irradiance	20

7.3	Atmospheric Effect	20

7.4	Poor levels of visibility	20

7.5	EMC impact (Lightning)	21

7.6	climate change impacts	21

8	Installation	21

8.1	Mounting methods	21

8.1.1	Self contained	21

8.1.2	Buoys	21

8.1.3	Lighthouses	21

8.2	Orientation	22

8.3	WINDLOADS	22

8.4	Shadowing/Shading	23

8.4.1	Double-face modules	25

8.5	AC connected – IS this used in a marine environment?	25

8.6	Identification of modules	25

9	Problems / failures	26

9.1.1	If lightning strikes :	26

9.2	Poor connection between cells	27

9.3	Hot spots	27

9.4	Micro cracking – wind pressure	28

9.5	Physical Stresses	28

9.6	Water ingress	28

9.7	Sealant failure	29

9.8	Delamination	29

9.9	Cell corrosion	30

9.10	Metal corrosion	30

9.11	Poor insulation	31

9.12	Mechanical impacts caused by handling and shock/vibration	31

9.13	Wave loading	31

9.14	Ice	32

9.15	Theft of modules and ways to prevent it	32

9.16	Connector failure and use of connectors and types	33

10	Maintenance and testing	33

10.1	Equipment and measurement devices – Some info from Peter S	33

10.2	Life / aging	34

11	Procurement	34

11.1	Assessment	35

11.1.1	The guarantee:	35

11.1.2	Price list :	35

11.1.3	Manufacturer	35

12	Recycling and repurposing	35

13	Standards	35

14	DEFINITIONS	36

15	ACRONYMS	36

16	REFERENCES	36

17	documentation	37

17.1	proofs	37

17.2	references	37

17.3	datasheet	37

17.4	(Example Heading level 2)	37

17.5	(Example Heading level 2)	37

18	AIMS AND OBJECTIVES (Example Heading level 1)	37

19	Example Heading level 1	37

19.1	(Example Heading level 2)	39

19.1.1	(Example heading level 3)	39

20	Example Heading level 1	39

20.1	TABLES	39

21	FIGURES	40

22	DEFINITIONS	41

23	ACRONYMS	41

24	REFERENCES	41

ANNEX A	SPECEMIN SOLAR MODULE SPECIFICATION	42

APPENDIX 1	EXAMPLE OF AN APPENDIX TITLE	43

ANNEX B	(EXAMPLE ANNEX TITLE)	44

ANNEX C	PERMITTED COLOUR PALETTE	45

List of Tables

Table 1	Example of a table caption; table with the significant information in the first column	20

Table 2	Example of a table caption; table with the significant information in the first row	21

Table 3	Example of a table caption; table with coloured rows	21

Table 4	Example table caption	23

List of Figures

Figure 1	Component of a solar system by Rfassbind - Own work, Public Domain,	8

Figure 2	Types of solar cells	9

Figure 3	Intercell connectivity	10

Figure 4	An example of a module with 6 parallel sections	11

Figure 5	Example from WSV showing the solar modules within dark sections on the daymark	11

Figure 6	Domberskjera lighthouse with white solar modules	12

Figure 7	An example of digital, ceramic printing on glass (Left) and yellow solar cell (right)	12

Figure 8	Details of the diode arrangement within a solar module.	14

Figure 9	Figure showing the construction of a solar module from www.sunnectsolar.com	14

Figure 10	Figures showing the application of flexible solar module from Trinity House and Rijkswaterstaat	15

Figure 11	Figure showing an example of anti-condensation heater in a solar module.	16

Figure 12	Thermal Characteristics	19

Figure 13	Diagram of atmospheric effects.	20

Figure 14	Example from China MSA of damaged solar modules following a super typhoon	22

Figure 15	Add title	23

Figure 16	Example of shadowing on buoys	24

Figure 17	Example figure caption	40

Figure 18	Another example figure caption	41

List of Equations

Equation 1	Wind pressure	16

Equation 2	Simplified wind pressure	17

Equation 3	Geographical range	39

Equation 4	Theory of Special Relativity	39

# INTRODUCTION

The use of solar panels on marine aids to navigation (AtoN) dates back to the mid 1980s, where the aim was to adopt a clean renewable energy source. This new source of energy allowed the powering of remote and afloat AtoN, removing the need for the delivery of Acetylene gas or Diesel to power light source.

Since these early days, the development of solar modules has made significant strides, moving from niche areas as small DC systems, to the mainstream power production, in the form of grid connected “solar farms”. This has delivered great enhancement in the performance of solar cell and a reduction in manufacturing costs, but it has resulted in manufacturers focussing their products on this high-volume market.

Naturally, the demands and requirements for such high volume “solar farm” panels differ to that required in a remote location marine environment. This has resulted in the challenge of trying to identify the qualities that make a good marine solar modules from that presented in a data sheet of the more mainstream panel. This guideline hopes to present the areas that are important to a survivable marine solar panel.

# SCOPE

This guideline has been developed to assist AtoN manufacturers and authorities, when selecting and applying solar modules to power systems in a marine environment. It is intended to inform the reader about factors influencing performance and reliability, as well as considering aspect of selection, application and purchasing. In addition, a sample  specification capturing some of the key factor to specify when engaging the market are presented in Annex ?

# THE USE OF SOLAR AS A POWER SOURCE FOR ATON

Although the first solar panel was created in 1881 by Charles Fritts, it was not until 1957 that the first commercial solar cells became available. This technology was fist adopted on AtoN in the mid 1980, generally as trials, leading to adoption in the mainstream as a source of power in the mid 1990. This technology initially allowed the replacement of small acetylene gas AtoN such as that used on buoys.

As the efficiency of solar cells has developed through the expansion of commercial mainstream solar modules for such things as domestic and industrial solar generation. This has allowed solar to be adopted on significantly higher energy demand system at one end of the power spectrum, with the development of small self-contained AtoN, often referred to as Integrated power system lantern (IPSL) at the other.

To meet the increasing power budget for these  solar system,  the number cells, modules, panels and arrays have expands. To aid in how these different components of a systems are referred to has been captured in figure 1, starting from solar cells used on an IPSL to solar arrays used on a larger lighthouse installation.

When developing the design of a photovoltaic power system, IALA provide guideline G1067 on how to design a photovoltaic power system.

Component of a solar system by Rfassbind - Own work, Public Domain,

## How to recognize the best photovoltaic panels on the market?

It is difficult for a neophyte to verify the quality of a solar panel by only checking the visual aspect. Indeed, several criteria such as standards and technical specifications will have to be assessed to ensure the reliability. Even then, it is only time in the operational environment that delivers this confidence.

# TECHNOLOGY

There are a number of solar cell technologies available, with many enhancements and variation being progressed in development laboratories around the world, but those commonly available are described below.

## Monocrystalline

It is made from the mineral "silicon", which is found in abundance in sand. A single "grown" crystal is gradually formed into a block. The cells are then cut into thin slices from 250 to 350 μm. The efficiency limit of the crystalline cell is around 35%. Currently this type of cell achieves efficiencies of up to 21%. These can be recognised by their dark colour and uniform structure.

## Polycrystalline

It is made from molten silicon glass that is formed in a mould. It is cheaper than the monocrystalline cell, but its efficiency is limited to  32%. Currently this type of cell achieves efficiencies up to 19%. It is recognized because its colour is irregular and clearer than the monocrystalline and has a rectangular shape without cuts at the edges.

Polycrystalline cells are somewhat less efficient than monocrystalline cells but are more efficient when the sun reaches low incidence angles on the solar cell.

## Thin film / flexible modules

It uses a new technology consisting of a thin film of pure silicon glass on a glass or ceramic substrate. This layer does not exceed 20 μm. The thickness of the entire cell is between 300 to 800 μm. The substrate may also be plastic which allows the production of flexible modules.

Currently the efficiency of these cells is around 13% although in laboratories efficiency levels of 15% have been reached. The advantage of this technology is that it is much cheaper to produce than the crystalline cells, it allows the formation of flexible modules and in the manufacturing process no polluting elements are used. However, they have a performance less than half that of crystalline type cells.

Types of solar cells

## Monocrystalline vs Polycrystalline panels

Crystalline silicon PV cells are the most popular solar cells on the market today and provide the highest energy conversion efficiencies of all commercial solar cells and modules. Silicon is safe for the environment and one of the most abundant resources on Earth. Monocrystalline panels, as the name suggests, are made out of a higher-grade silicon and their single-cell structure creates minimal resistance to the flow of electricity once the electrons are excited by the sun. Solar modules are constructed using a collection of these cells interlinked to achieve the desired voltage and power. It was once the case that polycrystalline solar panels were 20-30% cheaper than monocrystalline solar panels because producing monocrystalline cells was a more expensive process than producing polycrystalline cells, this however is no longer the case with the price difference between the technologies being negligible.

With all solar cells, electricity production falls as temperature goes up. Studies have shown that in the summer months with high temperature, polycrystalline and monocrystalline modules perform similar however, in non-summer months, even with similar irradiance, monocrystalline modules perform better then polycrystalline modules. The choice between monocrystalline and polycrystalline solar panels is not considered a critical factor when purchasing solar panels unless modules are susceptible to long periods of low irradiance in which case monocrystalline panels would be recommend over polycrystalline.

# MODULE DESIGN

This section looks at some of the important factor in the design of reliable marine solar modules.  When considering the design a solar system, then guideline G1039 on designing solar power systems for marine aids to navigation (Solar sizing tool) should be used.

## Number of cells

Each solar cell within a solar module produces about 0.5V at 25°C under standard test condition. This mean the solar cells within a module are interconnected in a series and parallel arrangement to achieve the desired output voltage and power. Typically for a 12V modules this is 36 cells in series to allow a suitable output for the charging range of a 12V battery system at different operating temperatures.

Modules designed for domestic grid connected purposes will have a higher output voltage and more solar cells in series, typically 72, as the drive is to maximise the voltage and efficiency of the modules.

## Intercell connection

The series / parallel connectivity of the solar cells within a module are achieved through the use of solder coated ribbon strip, soldered to a front and rear printed electrode on the solar cell. The series solar cells are connected in parallel by busbar ribbons at the top and bottom of the module. These busbar ribbons are then brought out to a junction box often on the rear of the module.

Intercell connectivity

The joining of the ribbons, both on the solar cells and to the busbars is achieved through a soldering process that can induce thermo-mechanical stresses. The ribbons are also bent over the cell edges, which can cause mechanical stress.

In  striving to maximise the output of solar modules thinner tapes are used to minimise the impact of shadowing on each cell. These tapes are subject to thermal stresses on a day-to-day basis which can lead cracking and premature failure. This is most likely in location where high daytime and low night time temperatures occurs.

The design of the intercell connectivity can impact on how well the solar systems perform. On paper, it looks as if striving for modules with the greatest efficiency is best, but in a marine environment, these modules are often fitted where small amounts of shading may occur due to supporting structures or hand railing within in the vicinity.

Shading can therefore lead to a period of reduce or no output from a module or part of a module. Given this, it is worth considering a less efficient module overall, but one with greater parallel sections. This will then ensure some output from a module during periods of partial shade, probably leading to a more effective solar system as a whole. When fitting the modules consideration should be given to orientating the parallel section in line with the possible source of shading to minimise any impact.

An example of a module with 6 parallel sections

## Colour

The colour of solar modules is generally a dark blue or black to maximise the energy capture, see figure 5. This however can have a detrimental impact on the look of the daymark, such that the solar modules need to be located with the daymark in mind. See figure 6.

Example from WSV showing the solar modules within dark sections on the daymark

The use of coloured solar modules on AtoN is a new area of development, predominantly driven by architectural building pressures, but is slowly becoming more readily available. This option has not generally been considered as an option on AtoN, but the efficiency of conventional AtoN and solar modules having improved, there is now not the need to maximise the available space for energy generation. This potentially allows the option to adopt coloured module of a lesser efficiency to improve the daymark. An example of this has been tried on the Norwegian lighthouse of Domberskjera as can be seen in figure 7.

Domberskjera lighthouse with white solar modules

There are a number of approached to achieving a coloured module, including colouring the solar cells, colouring the glass, but one of the most effective method is through the uses digital, ceramic printing of small coloured dots on the glass. This option provides the highest number of colour option along with a stable colour for a >20-year life, but with approximately 20% reduction in the solar module performance.

An example of digital, ceramic printing on glass (Left) and a yellow solar cell (right)

## Shock and vibration

The impact of shock and vibration is generally not an issue for the design of the solar modules due to the bonded sandwich construction. This can also generally be mitigated by the design of the supporting structure and if the module has a supporting rear structure. The design does need to consider the handling and environmental condition and as such should be consider “rugged” for this application.

## Module efficiency

Solar. module efficiency is the portion of sunlight energy that can be converted into electricity via the photovoltaics solar cell. For example: a solar panel with 15% efficiency and an area of 1 m² will produce 150W under Standard Test Conditions (STC). Where standard test conditions are with the module at a temperature of 25C, the level of irradiance is 1000W/m2 and an air mass of 1.5 spectrum.

The overall efficiency of the modules and the efficiency of the cells will be different, with the efficiency of the module being lower. This is as a result of spaces needed between the cells, the boarder of the frame and the inter cell connections all having an impact on available silicon area being exposed to the sunlight. Generally modules can be obtained with an efficiency between 12 and 20%.

It should be note that the efficiency of the solar module is just one factor in the efficiency of the power generation system and that it is important not to just focus on the module efficiency but consider the efficiency of the system as a whole and the transfer of power across the system.

More recently, trials have demonstrated thatthe efficiency of a whole module or system can enhanced by up to 80% through the addition of external devices such as a fressnel lens.

## Diodes

A solar module will ideally have diodes fitted either within the module junction box or sometime within the module laminate. These diodes have two different purposes and are known either as a bypass diode or a blocking diode.

The bypass diodes limit the impact shading has on a module. These are physically fitted within the panel but can be fitted in a junction box attached to the solar module. The bypass diodes allow a section of series cells to continue to provide power at a reduced voltage, rather than no power, if part of the series string is shaded. Ideally, one diode would be fitted across each cell, but this would be very expensive, so generally they are fitted to section within a module.

The blocking diode are used to prevent a shaded module acting as a load when modules are in parallel. These are usually within the junction boxes on the back of the panel. Where there is diffused light, perhaps from a module pointing a Northerly direction, then these diodes need not be adopted, as the diffused light will provide some output from the module.

As an alternative approach to the fitting of blocking diodes, each module can have a regulator fitted, such that the power output from the module is managed by the regulator based on the irradiance level. This provides excellent levels of redundancy but can be expensive.

## Regulator

Unregulated modules or modules fitted with regulators.

Details of the diode arrangement within a solar module.

## Construction of modules

The construction of all solar modules is made from a three-part laminate, essentially sealing the selected solar cell technology between two other supporting materials and using Ethylene-vinyl acetate (EVA) sheet as a waterproof bonding layer for the laminate. For flexible solar modules, thin film solar cells are used within a flexible plastic laminate, but for rigid solar modules, the monocrystalline and polycrystalline cells can be used with a supporting stiffening material as part of the laminate as show in Figure 10

Figure showing the construction of a solar module from www.sunnectsolar.com

### Glazing material

Both toughened glass and acrylic can be used as the glazing section. The use of acrylic allows a small degree of flexing during impact, without loss of the module. It also reduces the weight which benefits handling. The transmissivity of acrylic can also be better than toughened glass.

### Backing material

Various types of backing materials have proven to be successful in a marine environment. These being Polyvinylfluorid foil as a frameless arrangement where it is supported within a structure, marine grade aluminium where structural support is needed and stainless steel for standalone arrangement. A glass / glass structures within a frame have also been used when the solar modules are land based and protected from direct action by the sea.

The use of rigged solar modules, with a crystalline solar cell, has to-date been more popular than that of flexible thin film solar modules. This has generally been driven by the demand to maximise power generated however, the adoption of flexible modules generally on buoys is now starting to be used. Examples of these are shown in figure 11.

Figures showing the application of flexible solar module from Trinity House and Rijkswaterstaat

## Quality

Think about quality within the production process. How to measure performance. confirmation of performance VI curve.

Physical quality in production – this is captured as part of the whole document.

The quality of the photovoltaic solar panels is an important factor to consider for any marine solar power system. Indeed, the quality of the chosen photovoltaic modules will determine the reliability, operational life and output performance in the long term.

Think about the quality of the materials, especially the bonding materials over the life of the module.

## Ingress protection

This is a critical aspect to the long-term operation of a module in a marine environment. It is not just critical for the module itself but also for the junction box.

Junction boxes ideally need to be sealed to the modules with the junction box potted to prevent water ingress. The bonding between the module and junction box needs to be secure both to avoid any water ingress but to the physical effects of handling that could result in the ingress protection failing.

It is also important to ensure that during the production process there are no voids or gaps crated within the solar module laminate or the junction box where moisture can penetrate.

## Humidity and condensation

Humidity in a high temperature environment can cause similar impacts to that of direct water through the build-up condensation. To limit the impact of condensation, some modules provide an anti-condensation heater within the junction box providing a low level background heating to the module.

ADD PHOTO from Eng Soon.

An example of an anti-condensation heater in a solar module.

## Wind loading

When considering and selecting a solar module for applications on AtoN another key factor to survivability is understanding the modules maximum wind loading. The impact of this is covered in two parts; the first being the static pressure the module is designed to tolerate and still operate without issue. This is covered here, with the second being associated with the mounting and protection methods, which is detailed in the installation section.

Information on maximum gust wind speeds in different locations, especially remote locations, can be difficult to obtain and certainly varies. For example, a typical maximum for Germany is 40m/s, but for China this can increase to 70m/s during a super typhoon. As such the build and materials used may need to be different to provide the differing levels of performance.

To assess the forces involved, the wind loading pressure can be calculated as expressed in equation (1):

Wind pressure

Wp=0.5rv2g

where:

Wp is wind pressure (N/m2);

r is air volumetric weight (kg/m3);

v is wind speed (m/s); and

g is gravity constant (m/s2).

This formula is a general formula for estimating wind pressure by wind speed. It should be noted that air gravity and gravity acceleration vary with latitude and altitude. Generally speaking, r/g is smaller on the plateau than in the plain area, that is, under the same wind speed and the same temperature, its wind pressure is smaller on the plateau than in the plain area. Because the Aton is generally located near the sea (river) shoreline and the air volumetric weight and gravity acceleration are less affected by the height.

Given the above and assuming the following standard condition:

Pressure = 1013hPa;

Temperature = 15°C;

Air volumetric weight (r) = 0.01225 kg/m3; and

Gravity (g) = 9.81m/s2 at a latitude of 45°.

the above formula can be simplified to

Simplified wind pressure

Wp=v21600

As an example this formula is then used to calculate the force being applied to a typical solar module of a size 0.6m x 0.3m.

Sample wind loadings for a given module

| Wind speed (m/s) | Module stress(N) | Wind speed (m/s) | Module stress(N) |
| --- | --- | --- | --- |
| 0.0-0.2 | 0.00 | 24.5-28.4 | 90.74 |
| 0.3-1.5 | 0.25 | 28.5-32.6 | 119.56 |
| 1.6-3.3 | 1.23 | 32.7-36.9 | 154.01 |
| 3.4-5.4 | 3.28 | 37 ~ 41 | 192.82 |
| 5.5-7.9 | 7.02 | 42 ~ 45 | 239.09 |
| 8.0-10.7 | 12.88 | 46 ~ 51 | 291.47 |
| 10.8-13.8 | 21.42 | 52 ~ 59 | 352.80 |
| 13.9-17.1 | 32.90 | 60 ~ 61.2 | 421.36 |
| 17.2-20.7 | 48.21 | >61.2 | >422.74 |
| 20.8-24.4 | 66.98 |  |  |

For addition information on extreme weather condition see guideline G????

## Electrical Performance

The operational life for which  a solar module can generate power may be many decades. During this period the module power output slowly reduces over time from its initial 100% performance. Generally, manufacturers provide a guaranteed output performance over a time frame. This is often represented in a graphical form as shown in figure 12

Typical example of performance over time. This is from SolarWorld.

This power output will continue to be produced and reduce beyond the guarantee period until total failure occurs. This reduction in output can be caused by many things including cell damage, contact corrosion and antireflective coating deterioration. Ultimately total or partial output is lost generally due to one of the causes captured in section 8.

When designing a photovoltaic system, the minimum power requirement should be specified and taken into account when selecting the modules. Using the IALA solar model, guideline 1039, this is based upon a minimum output of 80%.

Currently available modules typically provide a performance output of 90% after 10 years and 80% after a further 25 years, defining the maximum operational life of a system, but if a life beyond this timeframe is needed then care is required when selecting the module.

## Operating conditions – Part of environmental factors?

# ENVIRONMENTAL FACTORS

When considering the use of solar as a power source, the first obvious thought is green energy with no further harmful emission, but the very production of solar modules is not wholly environmentally friendly and still has an impact on the environment.

## Materials used in production

There is a significant difference when considering solar power as a source of energy to that of other traditional forms, in that it is one of the few that does not produce harmful emissions or toxic waste in normal operation, but this is not the case for their production.

From an environmental perspective the production of solar cells uses a number of raw materials, such as silicon (Si), cadmium (Cd), tellurium (Te), copper (Cu), selenium (Se), and gallium (Ga), all of which are mined, followed by extraction and purification processes during which chemicals and significant amounts of energy are needed.

The first step is transforming quarts into metallurgical-grade silicon, using large amounts of energy in a furnace. This is then transformed into a purer form of silicon, known as polysilicon using a distillation process which is achieved using hydrochloric acid, but unfortunately it also produces a very toxic waste product called silicon tetrachloride. For which about three or four tonnes is produced for each tonne of polysilicon. However, at least 98.5% of silicon tetrachloride can be recycled as part of the production process. The output from this process is a bricklike ingots of polysilicon.

This highly pure polysilicon can then be grown into monocrystalline ingots using the Czochralski method. This method takes a seed crystal of silicon which is dip  into melted polysilicon. This is drawn and rotated to create a single crystal ingot. It is also during this process that the Boron doping is added creating P-type silicon. Again, this process requires high temperatures and significant amounts of energy.

These monocrystalline ingots are then sliced into wafers. Hydrofluoric acid is then used to remove any impurity generated when creating the wafers, but is also produces a textured surface, which helps reduce surface reflection. Unfortunately, hydrofluoric acid is a highly corrosive chemical that can destroy tissue and decalcify bones, so needs to be handled with care.

The next step is the creation of the solar cells from the wafers. This is achieved through doping (adding impurity) to the silicon wafer. Boron was added to the wafers as the monocrystalline ingot was created, producing p-type silicon and the n-type silicon is create by add phosphorous to the silicon wafers using thermal diffusion. To achieve this the wafers are sealed back-to-back and placed in a furnace in the presence of phosphorous gas, at a temperature just below the melting point of silicon. This again uses significant amounts of energy.

The creation of thin film solar cells eliminates many of the environmental and safety hazards from manufacturing, because there’s no need for certain problematic chemicals—no hydrofluoric acid, no hydrochloric acid. But that does not mean you can automatically consider a thin-film solar cell as green. The doping of thin film cells is achieved using cadmium telluride and cadmium sulphide to create the two doped layers. These chemicals unfortunately containing the heavy metal cadmium, which is both a carcinogen and a genotoxin, meaning that it can cause inheritable mutations.

Although the process of generating solar cells uses significant power and hazardous chemical, at lease over the life of the solar cells the power aspect can be offset  by the power generated by the cells though part of their life. Typically this can be achieve within two and a half years.

## Operational factors

Although solar panels appear to be an inert object with a glass surface, no moving parts and all held together in a frame, it is influence by its operating environment for both performance and operational longevity. This section outlines the key factor to consider.

Two major factors that affect solar panel performance under normal circumstances are irradiance and temperature. There are also other factors that are area dependent such as shadowing salt film, dust and bird fouling (Guano) which all directly impact on the level of irradiance reaching the solar cells.

# Temperature

One of the factors affecting the life and performance of a solar module is temperature that it experiences which is caused by the environmental effects within its local area. Depending on the location, those at the north and south generally get colder climate at the expense of the daily available sun hours. This means that the solar panels perform at optimum efficiency due to the lower operating temperature. However, those panels that are installed nearer to the equator generally get hot all year round which translate to a drop in the panel’s efficiency.

The output voltage of a module is affected by the cell temperature and changes in a similar way as the output power. Therefore, every solar panel has its own thermal characteristics derived under Standard Test Condition to measure the loss known as the “temperature coefficient”. Generally, it is given as -0.45%/°C for Monocrystalline and -0.50%/°C for Polycrystalline panel.

Refer to IALA G1136: Providing AtoN services in extremely hot and humid climate for more info.

Temperature: refer to G1039 / 1.1.4 TEMPERATURE INFLUENCE and 1.1.5 THERMAL CHARACTERISTICS – Add Fig 3 from this guideline

Thermal Characteristics

7 - Temperature coefficient :

The temperature coefficient indicates the electrical behaviour of your solar panel from a standard operating temperature of 25°. The units of this coefficient are expressed in "% per ° C", so the lower the coefficient, the more efficient the solar panel is. Conversely, the higher the number, the less the photovoltaic module will produce in case of strong heat in early afternoon.

A high temperature coefficient is the sign of a solar panel of lower quality. A reasonable number is around 0.5%, so the best solar panels go down to 0.3%, while 0.7% indicates a poor coefficient in terms of performance and therefore a photovoltaic equipment not very reliable.

High levels of UV- does this have an impact on life through breakdown of PN junction? – Look up information about the reduction in output over life due to high UV

## Humidity

## Irradiance

Irradiance is known as the amount of solar power available per unit area. Symbol = I. Its units are represented by kW/m² or mW/m². It is one of the major factors that affects the performance of solar panels. How we install each panel to face the sun is very important. Due to geometric effects, it is always recommended that each panel is facing 90° perpendicular to the sun’s altitude angle (when it is at the highest point in the sky) to ensure that the panel can capture all the sun’s radiation.

## Atmospheric Effect

Atmospheric Effects consists of two categories, Direct and Diffuse Radiation. The photo below to illustrate the concept easier.

Impact of these effects

Solar constant = 1.36kW/m²

solar radiation at surface = 1kW/m²

Sun

Reflected solar radiation (albedo) from atmosphere

Dust particles

Clouds

Direct solar radiation

Diffused solar radiation

Atmosphere entry point

Earth’s surface

Diagram of atmospheric effects from maritime and port authority of Singapore

## Poor levels of visibility

Pollutants can have the same impact, less of an issue offshore, but could be on inland waterways through built up areas

Performance factors

## EMC impact (Lightning)

Damage can occur to your photovoltaic system due to a direct lightning strike or nearby. Investing in protection is all the more advisable if your installation is expensive. Lightning protection will be prioritized at lighthouse sites located in areas where the risk of lightning strikes is highest. In order to know the probability of lightning strikes, it is advisable to use a kerunic level map of the place in order to define the level of protection that will be adapted

## climate change impacts

- Refer to Guideline GYYYY

## Deposits

These factors impact on the maintenance frequency and sizing of solar system.

Snow, sand, pollution deposits

### Bird Foul (Guano)

While it is possible to prevent birds from landing on the solar panels using bird deterrent i.e. bird spikes, etc, they can still drop their droppings while flying. Over time if not rid of, it will become harden and form a similar shading effect that can drastically affect the panel’s efficiency.

### Salt

To prevent a salt film and dusts from forming on the panel’s surface, it is recommended to install the panels at an angle to induce a natural washing effect when the rain comes. This will help wash away the salt that is gathered on the surface.

### Dust

Dust is an issue in certain extremely hot environments and can cause several issues.

Dust can cover lanterns and day marks, severely impacting the range, can cover solar panels thereby reducing the ability to charge batteries and its abrasive nature can accelerate deterioration of AtoN components.

Dust can be of different physical properties, both industrial and natural, can cause different issues and require different controls and cleaning methods.

Excessive dust also poses health and safety related risks to AtoN personnel. refer to IALA G116 / 2.2.7. DUST

Solar constant = 1.36kW/m²

solar radiation at surface = 1kW/m²

Sun

Reflected solar radiation (albedo) from atmosphere

Dust particles

Clouds

Direct solar radiation

Diffused solar radiation

Atmosphere entry point

Earth’s surface

# INSTALLATION

When selecting a suitable module for a marine environment, there will be a balance between the need to generate the power and the number and size of the solar modules.

What sizes are used on buoys and what sizes used on lighthouse and why?

Size, weight, power, efficiency, performance

- Self contained Vs  discrete panels

- Think about lighthouse situation

Safety and handling

## Mounting methods

### Self contained

With self contained units are designed with the solar module integrated into the moulded in – replace whole unit on failure (less stressful environments??

### Buoys

The fitting of solar modules to buoys is generally achieve through direct fixing arrangement for security purposes, yet there is still a need to be able to simply remove and replace the modules following failure.

Add photo of rubber nuts Peter D

Consideration of physical protection to the modules

Buoy – removable and replaceable – Photo from Peter.

Lighthouse based – can be as stressed but are on a dedicated frame. Can be glass/glass in a frame

Photo from Ronan

### Lighthouses

## Orientation

- Refer to G1039 / 1.1.6 SOLAR PANEL ORIENTATIONDisposal/ recycling

- For mayor fixed AtoNs, where the area and size of solar modules is not an issue and it is likely that the structure is also used to host not only the lantern but other power consuming AtoN devices, a better efficiency of the solar array (up to 45%) may be achieved using sun followers. In the most common designs the solar modules are mounted on a structure driven by a computer controlled engine which moves the array to the most suitable orientation )horizontally, vertically or both) according to the Earth´s position around the sun in a specific time. Some parameters to consider for the application of sun followers are:

- Space availability

- Cost (installation and maintenance)

- Overall power consumption of the AtoN

## Windloads

When the wind is large, the solar panel of the Aton is easily damaged by the wind force, and the energy system of the Aton is broken down, which results in the extinguishing of the navigational light and brings hidden trouble to the safety of navigation.As shown in the following figure, the Aton solar panel is affected by typhoon, resulting in silicon plate rupture, support deformation, short circuit and so on.

Add examples from other authorities of solar module mounting

Example from China MSA of damaged solar modules following a super typhoon

Practice shows that different installation methods are also of great significance to the wind resistance of Aton solar panels. Compared with the following two installation methods,One is that the solar panel support is installed in the middle of the lamp platform, and most of the solar panel overlaps with the equipment platform from the vertical direction. The other is that the solar panels are installed on the outside of the equipment platform, and the solar panels do not overlap from the vertical direction.This leads to a situation that in the case of wind, the solar panel of the previous installation method is shielded by the equipment platform, and its wind resistance is much better than the second installation method.

Add title

As shown in the above two figures, the solar panel specifications are 20 W X 2, one is installed in the center of the equipment platform, the other is installed on the outside of the equipment platform. In special weather (such as typhoon weather), the first one benefits from equipment platform occlusion, and his wind resistance ability is obviously better than the latter one.

In August 2017, the super typhoon Hato landed in Zhuhai, causing a large number Aton in Gaolan waters where near typhoon landing site broke down. After the disaster statistics, we found the damage probability of solar panels using the second one installation is five times more than the first one, and these Aton using the first installation are also more prone to structural damage, drifting off-position, broken chain and other failures. It is found that the solar panel of the second installation mode is directly subjected to wind, which is easy to be damaged under the condition of large wind force. More importantly, it also causes the increase of wind and wave area of the whole Aton to a certain extent, which can easily lead to serious abnormal accidents such as structure damage and buoy drifting off-position.

In summary, the installation of the Aton solar panel will the increase the wind loading area of the Aton, while different installation methods have different increment . In order to improve the performance of the solar panel in extreme weather conditions, the installation method should reduce increment of the force surface as much as possible.

## Shadowing/Shading

It is always recommended to install arrays that have clear line of sight to the sun. Any shadowing caused by nearby buildings or trees can cause a significant reduction in maximum power point voltage therefore a reduction in the maximum power available from the array. Although temporary, meteorological factors like passing clouds caused during overcast days also affects the modules efficiency.

Solar modules should be usually oriented toward the equator to maximise power output. The tilt angle should be chosen with regard to insolation, geographic location, self‐cleaning capabilities, available space, etc.

In the case of floating Marine Aids to Navigation it is not possible to guarantee the orientation of the modules, so a reduction factor must be applied.

It should also be considered that solar modules are sensitive to the presence of small shadows, even a narrow shadow can significantly decrease the output power. For example shadows generated by vegetation, buildings, daymarks and handrails can cause problems and should be avoided.

| The above example of shadowing could result in a 90% reduction in power output. |  |
| --- | --- |
| The above example of shadowing could result in a 75% reduction in power output. |  |

Example of shadowing on buoys

In some locations, fouling of the surface may be an issue. In these locations, it is recommended to avoid horizontal placement and that solar panels are installed with an inclination that promotes self‐cleaning. refer to IALA G1039 / 1.1.6 SOLAR PANEL ORIENTATION

### Double-face modules

Double-face modules not only take advantage of the direct but also the diffuse and reflected sun radiation. They can be assembled using two single modules by fixing them back to back, providing an increment of the generated power up to 30 % using the same space, which an especially useful aspect in buoys. Attention must be paid to the overall cost, weight the orientation of the array and the distance and efficiency of the reflecting area where light colours would be preferable as they better reflect solar radiation.

## AC connected – IS this used in a marine environment?

Refer to G1039 / 1.1.3 CURRENT ‐ VOLTAGE CURVE

6 - Power tolerance:

This is the amount of power in real output of your solar panel. For example a 165W module with a +/- 5% tolerance could actually produce from 156.75W up to 173.25W.

The best photovoltaic solar panels have a "positive only" power tolerance, which means that you are guaranteed to get at least the specified output power from the panel.

For example: a 200W solar panel with a tolerance of +5% / - 0% will produce a minimum of 200W and a maximum of 210W.

Resistance to earth

Types and quality of the connection cable

Connectors

IP67/68

Junction box (disadvantages, fixing, tests….)

9 - The Boitier by Pass and the cables :

Turn the module over to inspect the finish of the By pass box. It must be siliconized in the correct way and the appropriate cable diameter. Check the By-pass diodes that will allow the solar panel to continue to produce even if there is shade on part of the solar panel.

- •	Plugs

Connecting the cells

Product history

Cable size from JB

- Construction and material of junction box

## Identification of modules

- Date of manufacturing

- Manufacturer

- Electrical performance

## If lightning strikes :

-  less than 500m away, overvoltages are induced by magnetic fields on your entire electrical installation.

-  Indirectly: the installations and the various electrical circuits can suffer serious damage.

-  directly: the high current destroys electrical installations with fire risks.

The external protection is used to protect against the direct impacts of lightning. It consists of a lightning conductor system. The lightning conductors capture the lightning and conduct the current to the earth. Long rods made of conductive metal are used which protrude above the photovoltaic installation to be protected.

Interior protection is the use of devices to protect against currents and magnetic fields that can damage interior installations. The essential device is the earthing system, which prevents discharges from passing through the electrical installations. At the photovoltaic installation level it is necessary to :

If your installation is not directly exposed:

-connect the frame of the modules to the earthing circuit.

-connect the frame of the photovoltaic module to the ground by an electric wire on the outside of the building.

-and of course, lead the grounding circuit to the grounding bar using a low impedance device.

If your installation is directly exposed:

connect the frame of the module to the lightning conductor with a wire capable of withstanding the lightning current direct the discharges to the grounding circuit with a lightning arrester installed before the DC input line of the inverter.

For more information about lightning you can use Guideline 1012 Ed 3.

And specifically, Paragraph 7.6.4 SOLAR PHOTOVOLTAIC ARRAYS:

Photo‐voltaic (PV) arrays are vulnerable to lightning damage, particularly where they are located at a distance from the main building. A separate earth termination should be installed locally, connected to the array mounting frame. This should be bonded to the main lightning earth using a bonding conductor of not less than 50 mm2, which should follow closely the route of the DC cables between the photovoltaic array and the main building. When assessing this requirement, the rolling sphere technique (see Table 1) should be used based on the required lightning protection level and taking account of the location of the photovoltaic array.

All cables should be run either on cable tray, in conduit/trunking or tightly against earthed metalwork/conductor tapes.

## Vandalism and shooting

plexi glass???

Presentation from Adam Hay on vandalism so if we can find out more on this.

## Theft of modules and ways to prevent it

Although in recent years there has been a considerable reduction in the theft of solar modules due mainly to the sharp decline in the purchase costs of panels, the replacement costs due to logistics for modules located in remote and difficult to access locations remains high and represents a very important consideration in the design of a photovoltaic installation. The risk of theft or unauthorised use of photovoltaic modules installed at AtoN sites warrants consideration of an effective anti-theft solution to protect the photovoltaic panels. The most commonly used method for securing solar panels is the use of security fixing screws in the end and mid clamps of the solar mounting system. The fixings require a special insert bit or key wrench to remove the clamps securing the panels to the mounting frame.

# PROBLEMS / FAILURES

Use of commercial modules are now starting to be used on island and shore

Diodes

## If lightning strikes :

-  less than 500m away, overvoltages are induced by magnetic fields on your entire electrical installation.

-  Indirectly: the installations and the various electrical circuits can suffer serious damage.

-  directly: the high current destroys electrical installations with fire risks.

The external protection is used to protect against the direct impacts of lightning. It consists of a lightning conductor system. The lightning conductors capture the lightning and conduct the current to the earth. Long rods made of conductive metal are used which protrude above the photovoltaic installation to be protected.

Interior protection is the use of devices to protect against currents and magnetic fields that can damage interior installations. The essential device is the earthing system, which prevents discharges from passing through the electrical installations. At the photovoltaic installation level it is necessary to :

If your installation is not directly exposed:

-connect the frame of the modules to the earthing circuit.

-connect the frame of the photovoltaic module to the ground by an electric wire on the outside of the building.

-and of course, lead the grounding circuit to the grounding bar using a low impedance device.

If your installation is directly exposed:

connect the frame of the module to the lightning conductor with a wire capable of withstanding the lightning current direct the discharges to the grounding circuit with a lightning arrester installed before the DC input line of the inverter.

For more information about lightning you can use Guideline 1012 Ed 3.

And specifically, Paragraph 7.6.4 SOLAR PHOTOVOLTAIC ARRAYS:

Photo‐voltaic (PV) arrays are vulnerable to lightning damage, particularly where they are located at a distance from the main building. A separate earth termination should be installed locally, connected to the array mounting frame. This should be bonded to the main lightning earth using a bonding conductor of not less than 50 mm2, which should follow closely the route of the DC cables between the photovoltaic array and the main building. When assessing this requirement, the rolling sphere technique (see Table 1) should be used based on the required lightning protection level and taking account of the location of the photovoltaic array.

All cables should be run either on cable tray, in conduit/trunking or tightly against earthed metalwork/conductor tapes.

## Intercell tape failure

This is a common cause of failure on solar modules as either loss of a section, which can result in a reduced voltage, or a reduction in power output. This failure mode is one that occurs within a very short time. The cause of such failures is predominantly due to thermal stress. This can sometimes be seen as fine breaks across the tapes at high stress points such as on the edge on the cells.

Tape cracking

Intercell tape cracking.

This is an example of a solar module from the 1990s where the connections failed. This is now a well know failure mode and new design and production techniques have essentially eliminated this over the solar module guaranteed period.

## Hot spots

Reduction of about 15%

A hotspot in a solar module.

Need more investigation for an example of a hot spot.

## Micro cracking

The solar cells used in the manufacture of solar panels are subject to stress at three stages. Manufacture, installation and through its environmental life. These stress cause micro factures in the silicon that reduce the life and hence output power from the panel.

There are various method to test for the impact of micro cracking during manufacture, with one of the most popular being the Voltage – Current (V-I) characteristic. Most micro cracking will occur through the life of a panel, caused by thermal cycles, wind vibration and shock vibration.

Detection of this is not easy and may be seen on the surface by what is known as “snail trails”. Alternatively, the need to measure the panel performance (V-I characteristic) will indicate the impact micro cracking is having.

An example of “snails trails” caused by micro cracking.

## Physical Stresses

The failure of a solar module

No examples of physical damage from hail.

Delicate needs care handling.

Colision with a ship

Physical protection can’t be added to the front but edge protection can be provided.

Generally this type is on structure which required frequent handling or exposed to traffic

The effects of physical stress on a solar module.

## Water ingress

Water ingress due to the

Wrong method of mounting – Glues to the structure. This resulted in mechanical stresses between the backing foil and the solar cells. The result was the failure of the sealant which allowed the water between the glass and the foil.

Consideration about and the impact of thermal movement.

Water ingress within a solar module.

## Sealant failure

Sealant can fail over time due to aging.

Sealant failure.

## Delamination

Need more info on these examples and cause.

Examples of delamination.

## Module discolouration

No impact on module performance, does not look very good. Caused by flux used on the tapes reacts over time and then discolours the surface.

Photo from RD

## Cell corrosion

The photo is of an old module mounting in the horizontal. Possible sealant damage. Possible water ingress resulting in cell corrosion.

Cell corrosion within a solar module.

## Metal corrosion

Dissimilar material corrosion – example from RD around fixing and dissimilar metal in LV

Cosmetic problems only

Difference between good and bad can be difficult to tell

Example of dissimilar materials on a solar module.

## Poor insulation

Example of conductivity between the solar cell power and the sea as a battery. Poor insulation can have a very rapid impact on the corrosion of the Aluminium. Example show impact after just 2 years.

Current passing from the module into the superstructure using the aluminium superstructure.

Impact of dissimilar metals from a solar module.

Add photos from lightvessel with modules corroded.

Diodes missing

## Mechanical impacts caused by handling and shock/vibration

Need some input Merge with Physical stress.

## Wave loading

These are relevant to the location to be applied but need to be considered. This was mounted on a buoy with no support behind it.

Effect of wave loading.

Modules can be lost and torn from the structure.

Location needs to try and limit the loss, plus any physical support to limit deflection.

## Ice

Peter S has some photos of  solar panels with ice. Peter to send presentation of panels with damage.

Immersion in water and water jetting for cleaning

Solar modules in ice is not often used as the extreme conditions tend to damage the modules.

An example of ice build-up on a buoy

Wavewash refer to G1136 / 2.2.4. b EXTREME WEATHER EVENTS

## Connector failure and use of connectors and types

Corrosion of connection. Cause is due to moisture being trapped.

Peter D to add photo

New modules MC4 industrial standard connector – not all MC4 connectors are the same.

## Junction Box Failure

- Material failure causes the boxes to become brittle and breakdown over time. Impact of UV.

- Failure of the junction box by coming off the module.

- Possible Photo needed.

# Maintenance and testing

See model course

Cleaning and surface finishes (self cleaning)

## Equipment and measurement devices – Some info from Peter S

Check the battery voltage is good then the modules could be good – risk is the battery can be the problem

Short circuit current measurement and open circuit voltage.

Clean and do not disturb. Only check when a fault occurs or if there is physical signs.

Sample checking of performance and when necessary

Measurement methods

Measurement of solar module and an example from HT equipment of a solar module tester

The measurement of the open-circuit voltage and the short-circuit current gives a first statement about the function of a solar generator. However, defects caused by shading or cell breakage may remain hidden.

Therefore, a complete current-voltage characteristic curve has the greatest significance for the proper functioning of a solar generator. To record such curves, devices are available on the market that allow on-site measurements and subsequent evaluation of the data by PC.

In the following a simple method is shown, with which a

measurement of the solar generator with "household remedy" is possible.

The open-circuit voltage Uoc and the short-circuit current lsc can be measured directly with an appropriate multimeter (caution when measuring the short-circuit current: When removing the measuring tips, an arc can remain if the system voltage > 50 V) is sufficient!)

To record the characteristic curve, the solar generator must be loaded with different resistances. Of course, these must be able to dissipate the resulting power.

Since the operating point of the solar module is typically in the area around the MPP and partial shading has the greatest effect on the characteristic curve there, a few measuring points should be recorded especially here.

The position of the MPP can either be taken from the data sheet or estimated from the open-circuit voltage and short-circuit current as described:

UMPP (0.75 .. 0.9) UoC

IMPP (0.85 ... 0.95) lsc

On/off site

Frequency

Standards

Certification

You have obtained the certificates, certificates of standards, laboratory tests and the quotation, then it will be wise to go through the documents and data sheet of the photovoltaic module and check the following 10 points:

## Life / aging

Replace on age or performance.

Performance over life 90% after 10 years 80% after 15 years.

Performance testing over the life

Refer to IALA G1039 /1.1.2 LIFESPAN

Operational life

Performance life

# PROCUREMENT

- How to specify

## Assessment

### The guarantee:

The manufacturer must at least offer you a solar panel with a minimum 25-year guarantee. What is the procedure for replacing my solar panel in case of failure? It is a good idea to ask the installer or the manufacturer if you have difficulty obtaining information on this subject, then it is a bad sign.

### Price list :

The cost of a photovoltaic solar panel is normally expressed in cost per Wc. Example: 0.85 euros/Wp for a 250 Wp solar panel which indicates a unit price of 212.50 euros.

Beware of very low rates on solar panels, it is generally the sign of a minimum quality equipment with sometimes dubious guarantees. Do not hesitate to ask for several quotes from several distributors or installers in order to compare.

### Manufacturer

Try to find out about the reputation of the solar panel manufacturer in search engines. How long has it been in the photovoltaic field, see the design of the website and the aspects dealing with the guarantee.  It is wise to see the exchanges on the forums concerning the manufacturer's brand, are they positive or negative?A guarantee of reliability:

The standards are a guarantee of reliability for photovoltaic solar modules, so installers and manufacturers are able to provide you with quality certificates for the solar panels they offer. There is also the possibility to download the certificates and test certificates directly from the manufacturer's website, for example the certificates for the manufacturer Qcells.

The TUV certificate ensures that the photovoltaic module has passed the rigorous tests carried out by the German TUV (Technischer Überwachungsverien) laboratory proving its resistance to extreme temperatures, accelerated ageing cycles, violent projections and fire.he quality of photovoltaic solar panels:

The quality of the photovoltaic solar panels is an important factor to consider for any rooftop or ground-mounted solar power plant project. Indeed, the quality of the chosen photovoltaic modules will determine the payback time of your solar power plant by guaranteeing you an optimum production of solar energy in the long term.

# RECYCLING AND REPURPOSING

Use after performance drops below 80% of there output.

# STANDARDS

The manufacture of photovoltaic modules is governed by several standards required by the IEC (International Electrotechnical Commission) in order to be sold on the international market. These may also be supported by national standards. Some of these are identified below for information.

IEC 61215: Standards for crystalline silicon terrestrial PV modules or;

IEC 61646: Standards for thin film terrestrial PV modules.

Both of these standards certifies a guarantee of quality in terms of compliance with electrical parameters and mechanical stability. The requirements of this standard refer to the design qualification and approval of photovoltaic modules for terrestrial application and long-term use.

IEC 61730: Standard for PV module safety

This standard, which deals specifically with the safety aspects of the modules, complements IEC 61215, which sets the electrical performance.

UL 61730: Photovoltaic module safety qualification

This standard specifically deals with the prevention of electric shocks, the risk of fire, and the use of the photovoltaic modules in the field of photovoltaic systems and personal injury accidents due to mechanical and environmental stress.

IEC 62716: Ammonia corrosion testing of photovoltaic (PV) modules ammonia corrosion

IEC 61701: Salt mist corrosion testing

IEC 60068-2-68: Blowing sand resistance testing

UL 1703: Standard for flat-plate PV modules and panels

EN60529 – Ingress protection

EN61140

503 from join research centre ISPRA – useful content but may not be current

# DEFINITIONS

What definitions do we need to add from the IALA dictionary?

Suggested text: The definitions of terms used in this IALA Guideline can be found in the International Dictionary of Marine Aids to Navigation (IALA Dictionary) at http://www.iala-aism.org/wiki/dictionary and were checked as correct at the time of going to print.  Where conflict arises, the IALA Dictionary should be considered as the authoritative source of definitions used in IALA documents.

# ACRONYMS

AtoN	Aid to Navigation or Aids to Navigation

IMO	International Maritime Organization (Acronym style)

# REFERENCES

Abcd

Efgh

SPECEMIN SOLAR MODULE SPECIFICATION

Need to develop a sample specification for a marine solar module

example of ANNEX heading level 1

Body text

example of annex heading level 2

Body text

Example of annex heading level 3

Body text

Example of Annex heading level 4

Body text

Example table caption

| No | Title/Topic | IMO References | Requirements | Possible Audit Questions | Remarks |
| --- | --- | --- | --- | --- | --- |
| 1 | Table text | Table text | Table text | Table text | Table text |
|  |  | Table text | Table text |  |  |
|  |  | Table text | Table text |  |  |

EXAMPLE OF AN APPENDIX TITLE

APPENDIX HEADING 1

Body text

APPENDIX HEADING 2

Body text

APPENDIX HEADING 3

Body text

Appendix Heading 4

Body text

(EXAMPLE ANNEX TITLE)

Introduction (Example Annex Heading 1)

Body text.

Example of ANNEX HEADING Level 2

Body text

Example of annex heading level 3

Body text

Example of Annex heading level 4

Body text

PERMITTED COLOUR PALETTE

The IALA colour palette is divided in 3 palettes of different level of hierarchy that has to be respected.

Corporate colours (Not shown)

IALA’s corporate colour palette is directly inspired from the colours in our logotype:

- dark blue

- white

- yellow

- gradient blue

Primary & secondary colours

The primary colours are to be applied in complement with the corporate colours.

This second level of colours gives rhythm and helps to segment our publications.

The secondary colours are used to highlight information, titles in a minor proportion only.

These colours can’t be replaced by other tints.

PANTONE PROCESS CYAN C CMYK : C 100

RGB : R 0 - G 159 - B 223

CMYK : 50 % OF THE TONE RGB : R 131 - G 208 - B 245

CMYK : 50 % OF THE TONE RGB : R 148 - G 217 - B 213

CMYK : 50 % OF THE TONE RGB : R171 - G 219 - B 233

CMYK : 50 % OF THE TONE RGB : R 178 - G 193 - B 237

PANTONE 326C CMYK : C 81 - Y 39

RGB : R 0 - G 175 - B 170

PANTONE 7703 C

CMYK : C 79 - M 2 - Y 10 - K 11

RGB : R 0 - G 181 - B 208

PANTONE 660 C CMYK : C 88 - M 50

RGB : R 64 - G 126 - B 201

CMYK : 20 % OF THE TONE RGB : R 212 - G 237 - B 252

CMYK : 20 % OF THE TONE RGB : R 213 - G 240 - B 237

CMYK : 20 % OF THE TONE RGB : R 216 - G238 - B 245

CMYK : 20 % OF THE TONE RGB : R 218 - G 223 - B 246

PANTONE 258 C CMYK : C 51 - M 79

RGB : R 153 - G 80 - B 159

CMYK : 50 % OF THE TONE RGB : R 201 - G 169 - B 208

CMYK : 50 % OF THE TONE RGB : R 183 - G214 - B 155

CMYK : 50 % OF THE TONE RGB : R 246 - G 174- B 135

CMYK : 50 % OF THE TONE RGB : R 157 - G 157 - B 156

PANTONE 739 C

CMYK : C 78- Y 95- K 5

RGB : R82 - G 174 - B 50

PANTONE 2347 C

CMYK :M 88 - Y 100

RGB : R 230 - G 56 - B 17

PANTONE COOL GRAY 11 C CMYK : K 100

RGB : R 87 - G 87 - B 86

CMYK : 20 % OF THE TONE RGB : R 232 - G 221 - B 288

CMYK : 20 % OF THE TONE RGB : R226 - G 238 - B 217

CMYK : 20 % OF THE TONE RGB : R 253 - G 224- B 208

CMYK : 20 % OF THE TONE RGB : R218 - G 218 - B 218

CMYK : 10 % OF THE TONE RGB : R 237 - G 237 - B 237

Guideline

Recommendation

Model Course

PRIMARY COLOURS

SECONDARY COLOURS