DRAFT IALA GUIDELINE No. 1008

ON

REMOTE MONITORING

AND CONTROL

OF

AIDS TO NAVIGATION

Edition 4

March 2008

EXECUTIVE SUMMARY These Guidelines on Remote Monitoring and Control have been prepared to assist members when they are considering providing a system for the first time, replacing an existing system or up-dating a system. The guidelines will enable members to establish the basic operational decision criteria and performance standards for these systems and provide a knowledgeable basis for equipment selection and purchase. These Guidelines are not intended to establish a new mandate to expand the use of electronic monitor systems. Rather, they are to provide advice on how to develop an effective, modern system when a management decision has been made to employ electronic monitoring

contents							Page No.

| 1. | INTRODUCTION ……………………………………………………………………….4 |  |
| --- | --- | --- |
| 2. | MONITORING – GENERAL ISSUES…………………...…………………………….4 |  |
|  | 2.1 | MONITORING METHODS ………………………………………………...……4 |
|  | 2.2 | PARAMETERS MONITORED …………………………………………………..5 |
|  | 2.3 | COMMUNICATION FORMAT …………………………………………………5 |
| 3. | OBJECTIVES OF REMOTE MONITORING AND CONTROL …………………..6 |  |
|  | 3.1 | PURPOSE …………………………………………………………………………6 |
|  | 3.2 | OPERATIONAL GOALS …………………………………………………….…..6 |
|  | 3.3 | STSTEM OBJECTIVES ………………………………………………………….6 |
| 4. | AIDS TO NAVIGATION TO BE REMOTELY MONITORED ……………………8 |  |
|  | 4.1 | FIXED AIDS ……………………………………………………………………...8 |
|  | 4.2 | FLOATING AIDS ………………………………………………………………...8 |
|  | 4.3 | OFFSHORE STRUCTURES ……………………………………………………..9 |
|  | 4.4 | AtoN AIS ………………………………………………………………………..9 |
| 5. | PARAMETERS TO BE MONITORED …………………………………….………..10 |  |
|  | 5.1 | INTRODUCTION ……………………………………………………………….10 |
|  | 5.2 | PRIORITIES ……………………………………………………………………..10 |
|  | 5.3 | AIDS TO NAVIGATION (AtoN)………………………………………………..10 |
|  | 5.4 | power supplies ……………………………………………………………..13 |
| 6. | outstation equipment…………………………………………….…………..15 |  |
|  | 6.1 | introduction ……………………………………………………………….15 |
|  | 6.2 | design considerations ………………………………………………….15 |
|  | 6.3 | local monitoring ………………………………………………………...16 |
|  | 6.4 | remote monitoring and control …………………………………..17 |
| 7. | communication links ……………………………………….………………...19 |  |
|  | 7.1 | GENERAL ………………………………………………………………………19 |
|  | 7.2 | PLANNING ……………………………………………………………………..19 |
|  | 7.3 | ENERGY CONSUMPTION ……………………………………………………19 |
|  | 7.4 | TYPES OF COMMUNICATIONS LINKS …………………………………….19 |
| 8. | display, storage and control……………………….……………………21 |  |
|  | 8.1 | introduction …………………………………………………….…………21 |
|  | 8.2 | display …………………………………………………………….………….21 |
|  | 8.3 | storage …………………………………………….………….……………...22 |
|  | 8.4 | control ………………………………………..……………………………..22 |
|  | 8.5 | security of computer based systems ……..………………………22 |
| 9. | integration with other systems ………………..………………………24 |  |
|  | 9.1 | maintenance systems …………………………..……………………….24 |
|  | 9.2 | navigation warnings and vts ………..……………………………...24 |
|  | 9.3 | route planning …………………………………………..………………..24 |
|  | 9.4 | ais base station networks ……………………………..……………..24 |
| 10. | maintenance and testing ………………………………..……………….…25 |  |
|  | 10.1 | general ……………………………………………………..………………..25 |
|  | 10.2 | outstation equipment ………………………..…………………………25 |
|  | 10.3 | base station equipment ……………..………………………………….25 |
|  | 10.4 | maintenance procedures ……………..……………………………….26 |
|  | 10.5 | maintenance personnel ………………..………………………………26 |
|  | 10.6 | maintenance philosophy ………………..……………………………..26 |
| 11. | documentation and training ………………………………………………27 |  |
|  | 11.1 | documentation …………………………………………………………….27 |
|  | 11.2 | training ……………………………………………………………………….27 |
| 12. | future development …………………………………………………………...29 |  |
|  | 12.1 | general ………………………………………………………………………..29 |
|  | 12.2 | developments ……………………………………………………………….29 |

1.	INTRODUCTION

The first version of this document was developed in 1998 based on a work item from the 1994 IALA Conference and a subsequent 1996 Survey of IALA members on their current and anticipated use of Remote Monitoring and Control Systems (RCMS).

10 years on the document has been updated to acknowledge the development in technology, wider availability and reduced costs of RCMS systems both in the AtoN field and more generally.

# 2.	MONITORING – GENERAL ISSUES

2.1	Monitoring Methods

There are a number of ways to monitor an Aid to Navigation (AtoN)

2.1.1	User Monitoring

The provider of the AtoN relies on information received from the user of the aid. Reliability of the system and the integrity of information are low. Prior information on the cause of failure and advance warning of an impending failure is not available.  Control facilities are not available.  The AtoN failure could contribute to an accident before users can be made aware of the failure.

2.1.2	Visual/Audible Monitoring

These systems can be used when the AtoN or associated indicator lights can be directly observed or heard. Both the reliability and integrity of the system depend directly on the reliability of the observer whose attendance may be part-time.  It is unlikely that information on the cause of failure and advance warning of an impending failure will be available.  Because the Attendant / Monitoring Operator is not employed full-time, some time can elapse between that occurrence and identification of a failure.  Control facilities are not available.

2.1.3	Attendants/Keepers

This method keeps the AtoN under either regular or continual observation. The reliability and integrity of the system depends directly on the reliability of the observer. This system has the advantage that, subject to his technical competence, a Keeper or Attendant can, in some instances, intervene to effect repairs in the case of a failure without waiting for a maintenance crew.  As the Keepers are on site, full control facilities are available.

2.1.4	Remote Monitoring

Generally taken to mean that the location of the person doing the monitoring is sufficiently remote from the location of the AtoN that some electronic communication medium must be employed, eg. Radio, Cellular Telephone, Landline Telephone, Automatic Identification System (AIS) or Satellite. Control facilities vary depending on the type of Remote Monitoring and Control System used.  A detailed description of various types of Remote Monitoring and Control Systems is included in Section 6.

2.1.5.	Mobile Interrogation Monitoring

The AtoN, such as a buoy, may be interrogated occasionally by a passing buoy tender or shore Attendant to verify the operation and condition of the AtoN.  Limited control capability may be available.

2.2	Parameters Monitored

The level of monitoring and the parameters to be monitored are discussed elsewhere in this document but they can be categorised as the AtoN state and the Engineering state.

- AtoN state. Generally the status (eg On or Off) of the AtoN is monitored.  For floating AtoNs, the position may also be monitored.

- Engineering state.  Additional parameters are monitored to indicate the health of the AtoN including redundant standby equipment and its supporting systems (e.g. battery voltage in the case of solar systems).

2.3		Communication Format

To improve the availability of information the remote monitoring system will generally be capable of obtaining information from the remote location in a variety of ways. Chiefly by:

- continuous on-line communications between the base station and the remote site.

- regular polling from the base station and on demand.

- periodic programmed reporting by the remote site. (eg 2 hours after sunrise and sunset or to suit the monitoring centre operators shift patterns).

- exception reporting. When a nominated event occurs or preset parameter is exceeded, this report is generated by the remote site and transmitted to the monitoring station.

- a combination of two or more of the above.

- Also with systems such as AIS key AtoN stations may also be relayed to local users in real time, along with additional services such as sea state and weather information.

3.	OBJECTIVES OF REMOTE MONITORING AND CONTROL

3.1		Purpose

When considering a remote monitoring and control system it is necessary to identify the purpose and use of the system.  Questions which arise include, why monitor, what  aids and systems should be monitored, what communications should be used, what records should be kept, etc.

3.2		Operational Goals

The typical operational goal of an Aid to Navigation (AtoN) is to provide a requisite availability of service and reduce as much as possible any down time.  Availability is proportional to the Mean Time Between Failures (MTBF) and inversely proportional to the Mean Time to Repair (MTTR).  MTBF should be increased and MTTR should be reduced as far as possible.  When planning his passage the mariner anticipates that the AtoN on his route will be functioning in accordance with the published characteristics laid down in nautical documentation and on charts.  In the interests of safety the mariner should be notified as soon as possible of any failures of AtoN.  A minimum Time to Detect is therefore necessary.  The availability of the AtoN can be maintained by identifying faults which reduce redundancy or, in due couse, that would directly result in an AtoN failure if no remedial action is taken.  AtoN availability can be affected by both the AtoN system redundancy and by support systems such as power systems, which must therefore be considered.  Similarly, security, intruder and flood alarm systems must be considered because of the threat such events may pose to the AtoN.  The cost effectiveness of the AtoN service should be maximised with the provision of remote monitoring and control.

3.3		System Objectives

The objectives of a remote monitoring and control system may vary depending on the policies of the administration, the type and importance of the AtoN being monitored, and the local conditions.  The designer of a remote monitoring and control system may not need to include all of the following objectives and will only select those which best suit the application.

- Provide information to the operator consistent with his level of competence.

- Provide controls to the operator consistent with his level of competence.

- Monitoring and control system reliability and availability must be comparable with the systems being monitored.

3.3.1	Identification of Failures (affecting AtoN system provider liability):

- Identify failure of AtoN to operate within published specification.

- Notify failure of AtoN within a time period consistent with the phase of the voyage in which the aid is used and the criticality of the aid for safe navigation.

- Compile and maintain a record of operation of AtoN.

- Confirm third party reports of failures to avoid unnecessary mobilisations

3.3.2	AtoN Availability

- Confirm operation of AtoN within specification.

- Identify faults which are likely to lead to AtoN failure if no repair action is undertaken.

- Identify faults which reduce redundancy and which therefore threaten the AtoN.

- Notify faults within a time period necessary to carry out repairs before failure of the redundant stand-by system.

- Reduce downtime and improve availability through use of remote control resets.

- Verify status of redundant systems through remote control testing.

3.3.3	AtoN Maintenance (affecting MTBF and MTTR):

- Reduce downtime through use of remote control resets.

- Testing of redundant systems using remote control testing.

- Reduce incidence of faults through identification of recurring faults using post mission analysis.

- Assist investigation of cause of faults and failures using additional monitored parameters.

- Assist investigation of cause of faults and failures using historical data.

- As part of Conditioned Based Maintenance, allow remote review of plant condition thus assisting in scheduling Maintenance visits to maximise MTBF.

3.3.4	AtoN Cost Reduction (affecting cost of providing AtoN service):

- Reduce maintenance visits through use of remote control resets.

- Reduce maintenance visits by testing of redundant systems using remote control testing.

- Reduce costs through identification of recurring faults using post mission analysis.

- Monitoring and control system costs should be in proportion to the cost and importance of the systems being monitored.

- Reduced maintenance visits through use of remote review of plant condition and utilising Condition Based Maintenance techniques to reduce Maintenance visits.

# 4.	AIDS TO NAVIGATION TO BE REMOTELY MONITORED

In general, the providers of AtoN monitor the operation by one of  the methods described in Section 2.

A decision must be made as to which aids merit the extra security offered by remote monitoring and control described in section 3. Typically the decision is strongly determined by the relative importance of the aid in the waterway aid system.

The AtoN facilities for which monitoring should be considered fall into the categories detailed below.

## 4.1	Fixed Aids

4.1.1	Major lighthouses and Stations are frequently remotely monitored. When doing so, all AtoN signals should be monitored.  These will include the main light, standby light, emergency light, sector light and fog signals where fitted.  Radio aids to navigation which include radiobeacons, with or without DGPS, and racons should also be monitored.  In addition, the ancillary equipment such as power supplies, intruder alarms, fire fighting and detection equipment should be monitored.

4.1.2	Minor lights are now relatively easy to remotely monitor., The Operating Authority may elect to monitor all or only the more navigationally important of these AtoNs.

4.1.3	Sector lights. Depending on the complexity of the aid and its importance in the waterway, consideration should be given to monitoring sector lights.

4.1.4	Leading lights. Depending on the complexity of the aid and its importance in the waterway, consideration should be given to monitoring leading lights.

## 4.2	Floating Aids

4.2.1	Lightvessels.  All AtoN signals should be monitored.  These will be similar to those fitted to major lighthouses with the exception of radiobeacons and sector lights.  Additional ancillary equipment may be fitted such as collision monitors and position tracking systems.  The output of the latter may be used to operate off station and riding lights.  Alternatively, a remote control may be provided for this function.

4.2.2.	Lanbys and Lightfloats may contain AtoN similar to those fitted to lightvessels and should be monitored.

4.2.3	Major buoys fitted with a light, racon and a position tracking system should be considered for remote monitoring

4.2.4	Other navigational buoys are now relatively easy to monitor, the Operating Authority may elect to monitor all or only the more navigationally important of these aids.

## 4.3	Offshore Structures

Offshore structures comprising oil and gas rigs have their AtoN approved by the Authority, but are generally monitored by the operator of the structure where the structure is manned.  Where the structure is not manned all AtoN signals should be monitored.

4.4	AtoN AIS

Where AtoN AIS is installed its basic function can, in part,  be checked by a normal RCMS system via equipment self test facilities.  However it is preferable to monitor the actual signal in space by the use of an AIS Base Station Network and appropriate analysis software.  Where such Base Station Network monitoring is in place, AIS can be used to monitor other AtoN equipment and support systems at the location without the need for an independent RCMS system.

# 5.	PARAMETERS TO BE MONITORED

## 5.1	Introduction

This section addresses the parameters required to monitor the status and condition of the Aids to Navigation (AtoN), to assist in with the analysis of the reason for failure and to enable the remote control of the AtoN, should automatic systems fail to function. It sets out to prioritise the parameters to be monitored indicating those most appropriate for a given system together with the control necessary to achieve maximum availability of the service.

## 5.2	Priorities

The parameters to be monitored may be prioritised into three levels. Controls proposed are those which are regarded beneficial to maintain the service, therefore no priority is attached to these parameters..

5.2.1	Level 1 - Status:  The primary aim of any monitoring and control system (MCS) is to indicate the operational status of the AtoN. These are called events, that is, occurrences that take place during the normal operation of the AtoN.

5.2.2	Level 2 - Condition:  A further aim of the MCS is to report failures or impending failures of any equipment and provide additional information that will enable the Operations and Maintenance Staff to identify and determine the reasons for any abnormal conditions that may exist. These are called alarms.

5.2.3	Level 3 - Analogues:  This level of monitoring is applicable to a most MCS enabling the analogue value of parameters such as voltage and current to be reported.  Basic MCS systems for minor lights or buoys may only have one analogue ie battery voltage.  By analysing this data to produce trends, Maintenance and Engineering Staff can review the events leading to a failure and may also be able to detect the onset of failures and enable corrective action to be taken to prevent complete breakdown and hence maximise availability.

5.2.4	Controls:  In order to test certain types of equipment and to reset fault conditions without visiting a station, control facilities may be incorporated in a MCS.  This can be used to increase AtoN availability and improve cost effectiveness by reducing maintenance costs.  The design of the interface between the MCS and the AtoN must be such as to not interfere with the operation of the AtoN in the event of failure of the MCS.

## 5.3	Aids To Navigation (AtoN)

Today’s mariner has an extensive array of AtoN to assist his safe passage ranging from buoys (lit or unlit), lanbys, light vessels, beacons (lit or unlit) and lighthouses.  Each may have a variety of AtoNs and hence monitoring and control requirements.  Individual AtoNs are discussed and parameters to be monitored and controlled together with their level of importance, as defined above, are indicated.

The following paragraphs concentrate on individual systems and list the parameters that are considered most useful in monitoring and controlling the AtoN and associated systems. It cannot be exhaustive but it indicates the principle behind the selection of parameters.

5.3.1	Navigation Light

A typical navigation light system consists of a main light, a standby light and an emergency light.  The main and standby lights are on a lampchanger while the emergency light is a smaller, separately powered light.

| PARAMETER | OPTIONS | LEVEL |
| --- | --- | --- |
| Main Light Status | On / Off | 1 |
| Standby Light Status | On /Off | 1 |
| Main Light Condition | Normal / Fail | 2 |
| Standby Light Condition | Normal / Fail | 2 |
| Nav Light Status | On / Off | 1 |
| Nav Light Condition | Normal / Fail | 2 |
| Emergency Light Status | On / Off | 1 |
| Emergency Light Condition | Normal / Fail | 2 |
| Penultimate Lamp Selected | Yes / No | 2 |
| Optic Drive A Status | On / Off | 1 |
| Optic Drive B Status | On / Off | 1 |
| Optic Drive A Condition(speed/character) | Normal / Fail | 2 |
| Optic Drive B Condition(speed/character) | Normal / Fail | 2 |
| Nav Light Control | On / Off | C |
| Emergency Light Control | On / Off | C |
| Nav Light Reset to Normal | Reset | C |

It is not only necessary to know that the light is ‘ON’ or ‘OFF’, but also that it is exhibiting the correct character/code and that the range of the light is achieved.  If any of these conditions are not met a main light fail signal should be transmitted which may be derived from monitoring the lamp current, the light output from a photocell and in the case of a lamp-changer an ‘out of position’ indication.  Failure of the optic rotation drives and hence light character should automatically cause the main light to extinguish and illuminate the emergency light. This in turn will cause a “nav light fail” to be transmitted.

5.3.2	Differential Global Positioning System (DGPS)

When DGPS is transmitted the above list should be augmented by alarms derived from the reference station and integrity monitor as follows:

| PARAMETER | OPTIONS | LEVEL |
| --- | --- | --- |
| Correction Age | On / Off | 2 & 3 |
| Message Error Ratio | On / Off | 2 & 3 |
| Beacon S.N.R. | On / Off | 2 & 3 |
| Beacon S.S. | On / Off | 2 & 3 |
| Numbers of SV's | On / Off | 2 & 3 |
| Horizontal DOP | On / Off | 2 & 3 |
| Position Error | On / Off | 2 & 3 |
| PR Residual | On / Off | 2 & 3 |
| PR Residual | On / Off | 2 & 3 |
| Low UDRE | On / Off | 2 & 3 |

Notes:	SNR	:	signal to noise ratio

SS	:	signal strength

SV	:	space vehicle

DOP	:	dilution of position

PR	:	Pseudo range

5.3.3	Racon

| PARAMETER | OPTIONS | LEVEL |
| --- | --- | --- |
| Racon Status | On / Off | 1 |
| Racon Condition | Normal / Fail | 2 |
| Racon Reset to Normal | Reset | C |
| Racon Position | On Station / Off Station | 2 |
| Racon Change Code | Normal / Morse D | C |

5.3.4    AIS (AtoN AIS and Base Stations)

(Details to be advised by E Nav Commmittee)

## 5.4	Power Supplies

The power used to drive the AtoN may come from many different sources dependent on the station location, energy requirements and the availability of services.  A mainland base station will normally have an AC mains supply available but will usually back this up with a battery and possibly a diesel alternator. An off shore station however is unlikely to have a mains AC supply and may derive its supply from a diesel alternator set or a renewable energy source such as photovoltaic solar, wind or wave power using batteries for energy storage.

Various combinations of power sources are used and three examples of these systems are described below:

- Mains with mains failure diesel alternator set

- Mains float charged battery system

- Photovoltaic solar powered battery system

5.4.1	Mains with Mains Failure Diesel Alternator

| PARAMETER | OPTIONS | LEVEL |
| --- | --- | --- |
| Mains Supply Condition | On / Fail | 2 |
| Generator Status | Available / On | 1 |
| Generator Condition | Normal / Fail | 2 |
| Fuel Level Condition | Normal / Low | 2 |
| Engine Fail to Start | Normal / Foil | 2 |
| Alternator Voltage | Normal / Low or High | 2 |
| Engine Temperature | Normal / High | 2 |
| Engine Oil Pressure | Normal / Low | 2 |
| Engine Speed | Normal / High | 2 |
| Starter Battery Charger | Normal / Fail | 2 |
| Alternator Current | Current in Amps | 3 |
| Generator Reset to Normal | Reset | C |
| Generator Control | Start / Stop | C |

A mains failure diesel alternator set would normally include a control cubicle monitoring its performance and providing trips and alarms to maintain the plant in a safe condition. To minimise the data transmitted by the monitoring system these trips and alarms are often combined to give a general alarm indication.

5.4.2	Mains Float Charged Battery System

| PARAMETER | OPTIONS | LEVEL |
| --- | --- | --- |
| Mains Supply Condition | On / Fail | 2 |
| Battery Charger Condition | Normal / Fail | 2 |
| Battery voltage | Normal / High | 2 |
| Battery Voltage | Normal / Low | 2 |
| Battery Voltage | Volts | 3 |

Where a charger alarm is not available, an alternative is to monitor when the battery voltage drops below the float voltage. A high battery voltage alarm should be set below the voltage at which the AtoN may be damaged.

5.4.3	Renewables (solar, wind, wave, etc) Powered Battery System

| PARAMETER | OPTIONS | LEVEL |
| --- | --- | --- |
| Regulator Condition | Normal / Fail | 2 |
| Battery Voltage | Normal / High | 2 |
| Battery Voltage | Normal / Low | 2 |
| Battery Voltage | Volts | 3 |

# 6.	OUTSTATION EQUIPMENT

## 6.1	Introduction

This section discusses the various types of monitoring and control equipment available and identifies some of the design problems that need to be considered during their selection and implementation.

The equipment employed on station to provide the required remote monitoring and control facilities will be directly dependent on the methods used, as discussed in Section 3.  These range from direct monitoring by the user to a fully automated AtoN where the systems are monitored and controlled remotely by a centralised base station.

The choice of method will largely be dictated by the operational requirements, by economics and available expertise.  What is appropriate in one part of the world where labour costs are low and technology is comparatively expensive, may be inappropriate where labour costs are high and technology is relatively inexpensive.

It should also be clearly understood that a primary objective of a lighthouse authority is to assure the availability of the AtoN.  Whilst a well designed and implemented outstation equipment can assist in achieving this goal, a poorly designed system may be detrimental and threaten their performance.

As described in Section 5, the information to be monitored by the outstation is dependent upon whether purely status information on the AtoN is required, or whether additional information to aid maintenance and to enable the prediction of future performance of the systems is necessary.

RCM equipment should meet approved international and national standards, such as ITU and local PTT standards in as much as they are relevant to the monitoring system.

## 6.2	Design Considerations

With the wide range of options available for outstation equipment, there are many considerations to be taken into account before a valued judgement can be made upon what type of system is best suited for a particular application and circumstance. For electronic systems open architecture formats should be selected to ensure that there is the maximum level of component interchangeability over the system lifecycle.

6.2.1	Design Philosophy

Simplicity is often the best policy particularly where technical expertise is limited. Well designed electronic systems are significantly more reliable than their electro-mechanical alternatives. However, the effort required to develop a proven system, particularly software should not be underestimated. Care should be taken during software development to ensure a structured approach thus minimising the design and commissioning effort of subsequent modifications.

6.2.2	Input / Output (I/O) Segregation

It is good practice to segregate monitoring and control functions such that failures that may occur in the control outputs do not affect the monitoring, leading to misleading indications. This can be achieved by ensuring that separate (I/O) cards are used for the two functions. Isolation is invariably provided between cards, but is less common between adjacent inputs on the same card.  It is also important to monitor the AtoN to confirm that a remote control action has caused the desired change in the equipment.

6.2.3	Energy Consumption

A further consideration is the energy consumption of the outstation. This is particularly important where energy is limited, such as photovoltaic solar powered stations in the more polar latitudes and with any system supported by battery back-up. The power consumption of micro-electronics has reduced as it has developed and consequently the requirements of the communications system have become a major proportion of the overall energy consumption calculation.  Transmissions can be limited by sending only data resulting from a change of state of an RCM input at the station. Where Maintenance and Operations Staff are required to record data at regular intervals, for example, for trending fuel consumption or battery voltage, this can be achieved by local data storage at the outstation. The data need only be transmitted to the base station when an alarm occurs which requires action by Operations Staff.

6.2.4	Computerised Systems

Computer monitoring and control systems present new problems from those experienced with hardwired systems. They operate at high clock rates with significant harmonics.  As a consequence they radiate RF energy and are susceptible to electro-magnetic interference, which can not only affect other computerised systems but also interfere with radio communications.

Whichever system is employed, it is likely that failures will occur. It is therefore important that the effects of these failures are minimised by implementing the ‘fail safe’ concept. As an example, signal relays (switching low currents), interconnections and power supplies, are more likely to fail open circuit. Therefore, a system should be designed such that in the event of failure, the AtoN remains operational and the monitoring system indicates an alarm. However, compromises will have to be made since maintaining a relay in its energised condition may have a significant affect on the energy requirement of the power systems employed.

## 6.3	Local Monitoring

6.3.1	Status Indications

Status information may be displayed in its simplest form by indicators on the control equipment, indicating whether the AtoN is ON, OFF or FAILED.  Where multiple systems are employed this information may be relayed to a local control point and displayed on an annunciator panel.

This type of display is ideal for local monitoring, since it facilitates the management of events and alarms, whereby:

- a change-of-state of the system has to be accepted in order to silence the audible alarm, and;

- a visual indication is displayed until it is reset at the source and then cleared from the display.

6.3.2	Maintenance

Further information can be made available to assist the maintenance of equipment by indications on equipment modules or electronic circuit boards.  These may consist of small light emitting diodes (led) at strategic points within the circuit indicating the operational status of the board; whether it is functioning or not.  Staff can then carry out front line maintenance by board replacement minimising the downtime of the equipment and maximising availability.

## 6.4	Remote Monitoring and Control

Over the years remote monitoring has developed from dedicated hardware solutions often utilising relays and simple indicator lamps or electro-mechanical devices, through to flexible systems employing distributed intelligent units such as Programmable Logic Controllers (PLC) software configured to give total control and monitoring.  This latter system requires a computer workstation for processing and display of information.  As all new systems will invariably be PLC based the earlier systems are not discussed further in this Guideline.  The key systems discussed are:-

- PLC/PC acquisition and control system

- PLC/PC integrated Supervisory Control and Data Acquisition (SCADA) system

- mobile interrogation systems

- AIS

6.4.1	PLC/PC Acquisition and Control Outstations

Programmable Logic Controllers (PLC’ are easy to install and are highly flexible in allowing changes to be implemented in software to manage digital and analogue signals for monitoring and control purposes.   The cost of simple PLC systems has reduced (in real terms) significantly over the years, and as a consequence has largely replaced even the simplest relay logic system.

The PLC/PC installed in outstations is commonly known as a remote terminal unit (RTU). The inputs and outputs from equipment being monitored and controlled are connected to the RTU.

6.4.2	SCADA Systems

Modern System Control and Data Acquisition (SCADA) systems  allow the integration of multiple data streams from PLCs, AIS and other devices facilitating a common user interface that incorporates control, data logging and alarm management. Sophisticated computer graphics packages are available which enable information to be displayed to suit individual user requirements. By simplifying the displayed information using appropriate screen design for the user interface to indicate the status of systems, monitoring can be undertaken by non-technical staff, whilst retaining all the information within the system for access by technically proficient Engineering and Maintenance Staff.

In some cases the actual base station may not be directly operated by the AtoN Authority.  Services are now available where the RTU communicates with a remote server operated by a contractor who provides monitoring services.  The AtoN status is then accessed by the AtoN Authority via a secure web site.

With the data available on a computer at the base station it becomes possible to integrate other activities into the system enabling planned maintenance and report generation. By connection to a suitable network further integration is possible with for example, the hydrographic service and vessel transit systems.

6.4.3	Mobile Interrogation Systems

A mobile interrogation system can be used by a passing buoy tender or local Attendant to check the status and condition of small AtoN and buoys.  A low energy consumption transceiver, installed on the AtoN, can be interrogated by a hand-held, mobile interrogator to report parameters such as lampchanger position and battery voltage.  A control channel can be used for test purposes. These systems may also log data, such as AtoN energy consumption or PV solar energy generated, to assist Maintenance Staff.

6.4.4	Automatic Identification System (AIS)

Where AIS is fitted to an AtoN the key status of the AtoN is transmitted on message 21 and this can be monitored via an AIS base station network.  Additionally most AtoN AIS units can be used to monitor associated system status such as battery voltage, this can then be transmitted via message 6.

# 7. COMMUNICATION LINKS

7.1		General

This section summarises the various communications media that may be used singly or in combinations to connect from a remote site to a control centre. The final selection of services will be dependent upon investment and running costs that are area specific, and the requirements for availability and data rate that require further detailed engineering studies.

7.2		Planning

When planning a communications system, a link analysis should be prepared to ensure that the type of link selected is sufficiently capable in terms of reliability, information quality, capacity and integrity, for the system it will serve.  Attention must also be paid to the capacity of the power supply to ensure that sufficient power is available to operate the system in both the low demand of routine operation, as well as the heavy demand of repeated failure transmissions and control centre interrogations.  The final choice of communications system is often an economic one.

7.3		Energy Consumption

Estimation of energy consumption is usually based on assumptions of daily transmit time and is calculated in watt-hours/day (wh/day).  The outstation is usually designed to cease attempts to communicate after a number of failed tries.

7.4		Types of Communications Links

There are essentially five main types of communications links:

- Public and Private Networks

- Radio Links

- Cellular Phone Systems

- Satellite Communication Systems

- Visual

7.4.1		Public and Private Networks

Public and Private Networks include PSTN, Leased Private Circuits, Owned or Non-leased Private Circuits ISDN.

.

7.4.2		Radio Links

Radio links are generally available utilising Medium Frequency (MF), High Frequency (HF) Very High Frequency (VHF), Ultra High Frequency (UHF) and Microwave Frequencies. Direct Satellites Links are an application of microwave links.

7.4.3		Cellular Telephone Systems

Cellular telephone systems can be used to provide facilities ranging from basic on/off switching to complete site control and monitoring. The availability for and speed of, data transmissions, on cellular networks may vary from system to system. Coverage, especially to seaward, may not be complete.

7.4.4		 Satellite Communications Systems

A number of  operators offer services for data transmission via satellites that can be used to provide all the requirements of a remote control and monitoring system.  The costs for air time may be significant and coverage is generally global apart from the polar region.

7.4.5		Visual Communications

Visual communications can be used in monitoring where a person is on duty near enough to see the AtoN or indicator lights.

# 8.	DISPLAY, STORAGE & CONTROL

## 8.1	Introduction

Display and storage will be dependent upon the sophistication of the type of monitoring and control used.  This may range from manual collection of data recorded on paper logs to fully automatic electronic monitoring systems where data will be retained and archived on electronic media.

Sections 5 and 6 give details of the parameters to be monitored and the equipment to be used.  No matter which system is employed, such as log sheets, visual indicators or electronic media, data should be displayed clearly and unambiguously.  It is normal practice to store data to assist in maintenance and event analysis.  It should be stored to facilitate its quick and easy retrieval whilst ensuring its preservation.  The method and length of storage are dependent on the requirements of the Authority.

## 8.2	Display

There are various types of display which fall into the following categories:

- Visual indicators

- Annunciator panels

- Visual Display Unit (VDU)

8.2.1	Visual Indicator

Visual indicators should be coloured to conform to normally accepted practice as follows:

'Red' 		indicating 	'Alarm'

'Yellow'	      "		'Warnings'

'Green'	      "		'Normal'

8.2.2	Annunciator Panels

Annunciator panels provide visual indications and audible warnings and their operation is described in Section 6.3.

8.2.3	Visual Display Unit

With the increasing tendency towards electronic monitoring, the VDU is the most common method of display.

The specification and size of the VDU will be dependent upon the amount of information to be displayed and the frequency of use.

Care should be taken to ensure that the design of the display and the colours used are acceptable for long term viewing.  However, alarms and warnings should be clearly indicated in contrasting colours.

For most monitoring system with other than a very few AtoNs VDU displays will be used. For such larger systems as they evolve and are extended there may be a number of monitoring methods and equipment being used. In such instances it is important to ensure that the user interface merges the various inputs in a coherent manner to allow the system as a whole to operate efficiently.

## 8.3	Storage

The type of data storage facilities required will depend upon the type and  quantity of data to be recorded, the required storage period and method by which the data was gathered.  The storage media available are:

- Paper

- Electronic

8.3.1	Paper

Manual monitoring systems normally use paper as a storage medium, for example, watchkeepers log book.  Log books are bulky and consequently require large storage areas.

8.3.2	Electronic

Electronic storage is more generally used and requires the minimum space for large quantities of data.  The electronic media may be in the form of magnetic tape or discs and optical discs (CD), the latter being more suitable for long term storage.  Because of the risk of corruption of data, electronic storage systems should include back-up facilities.

Where electronic storage is adopted there are significant benefits to be gained from recording key systems data over time to allow review of trends in assisting in identifying operational problems that may in time lead to an AtoN failure. Specifically for solar lights the trending of battery system voltage is very beneficial.

## 8.4	Control

When required, controls can be provided at the base station to operate outstation equipment, for example, navigation lights, diesel generators.  When designing the facility, care must be taken to ensure that inadvertent operation of a control function is not possible.  For example, this may be achieved by restricting access with the use of a password requiring confirmation of the control requested.

## 8.5	Security of Computer Based Systems

Access should be restricted to only those parts of the system that the staff require in order to carry out their duties.

The System Manager will require the highest level of access to the system enabling him to carry out system reconfiguration including software upgrades.

Engineers, whilst not having the above level of access will need a sufficiently high level of access to configure the database to introduce modifications brought about by changes to outstation equipment.

Operators require a lower level of access sufficient only to allow them to perform their monitoring and control functions.

Access can be restricted by the use of passwords.

# 9. INTEGRATION WITH OTHER SYSTEMS

Remote Monitoring and Control Systems present the opportunity for integration with other systems and business processes to have access to AtoN status information.

Some examples where Authorities have already begun this integration with systems include:

- repair and maintenance

- Navigation warnings

- Vessel Traffic Services (VTS)

- Route Planning System

- AIS Base Station Networks

## 9.1	Maintenance Systems

The RMC system can provide information to the Maintenance Department to enable speedy and efficient planning of equipment repair and a facility to control equipment for routine operation and fault finding.  Data can also be made available to plot trends in equipment performance in order to predict possible future failures.

It is desirable therefore when planning a system that the requirements of both operations and maintenance are considered together. It is likely that different users will require visibility of different types of information and control access right requirements will not be uniform for all users.

Remote access to the RMC system for maintenance staff provides significant benefits in the review of data immediately before attending site for a failure or planned maintenance.

## 9.2	Navigation Warnings and VTS

Outputs from the RMC database can be used to generate messages containing AtoN state and transfer these messages to one or more programmed addresses for broadcast to the Mariners as navigation warnings. It is not best practice for such broadcasts to be fully automated and there should be a human review of all the relevant circumstances before taking notification action.  At the present time the usual method of promulgating navigation warnings is via the Hydrographic Offices of that country.  Such messages could also be passed to a VTS control centre for direct broadcast to ships in the area.

## 9.3	Route Planning

It will be possible in the future to automatically send AtoN data from the RMC database to a shore based provider, for example, a web site on the Internet, enabling a navigator on a vessel to obtain this information in electronic format for route planning.

9.4 AIS Base Station Networks

Such networks with appropriate coverage and data processing software can monitor the status of AIS fitted AtoNs and the information merged with that of the Authorities RCMS.

# 10.	MAINTENANCE AND TESTING

## 10.1	General

Modern Control and Monitoring equipment use solid state technology which over the years has proven to be reliable. Due to the nature of its manufacture field repair is not usually practicable and repair by replacement policies are normally adopted.

## 10.2	Outstation Equipment

10.2.1	The system at the outstation can comprise the following equipment:

- Central processor containing circuitry that assembles parallel input data from the on-site plant eg. lights, radiobeacons, racons, power supplies etc. into a serial digital signal format.

- Equipment sensors and controllers to and from the on site plant.

- Signal processing unit for connection to the communications means

- A communications means (VHF,satellite,etc)

- Transmitter/receiver aerial.

- Power supply.

10.2.2	The equipment mentioned above at section 10.1 can be designed to operate with extended maintenance intervals (12 months or more). Maintenance visits should be carried out by suitably trained staff provided with adequate test equipment and documentation. A  maintenance visit would typically include the following items:

- Visual inspection of all equipment and connectors.

- Measure all system power supply outputs.

- Check all control and monitoring functions.

- Check communications link..

- Other items specified by the manufacturer.

## 10.3	Base Station Equipment

10.3.1	The equipment at the base station can compromise the following equipment:

- All equipment mentioned in Section 10.2.1

- Display and keyboard units.

- Data storage units.

- Recording equipment.

- Alarm units.

- Power supplies.

10.3.2	As with the outstation the base station equipment can be designed to operate with an annual or greater period between planned maintenance and would include the items listed at Section 10.2.2.

## 10.4	Maintenance Procedures

Maintenance procedures should be prepared to cover routine and breakdown / event maintenance.

Detailed maintenance procedures should be prepared prior to the commissioning of the equipment and include the following details:

- Equipment handbooks and diagrams

- Equipment performance criteria and working limits

- Equipment test procedures

- Equipment test results

- Equipment test equipment schedule

- Equipment repair documentation and repair procedures

## 10.5	Maintenance Personnel

Routine maintenance and repair can be carried out by each of the following methods:

- In house maintenance personnel

- Third parties

- Equipment suppliers

In all cases, maintenance personnel should be suitably qualified and trained in all aspects of the equipment concerned.

## 10.6	Maintenance Philosophy

Careful consideration should be given by the Authority operating the equipment to agree the philosophy to be adopted when carrying out maintenance on control and monitor equipment, for example:

- duplication of equipment to provide redundancy

- modular replacement

- who repairs module and turn around time

- in-house / third parties / suppliers maintenance and repair

- maintenance agreement

- software changes and upgrades

- remote diagnostics

# 11.	DOCUMENTATION AND TRAINING

## 11.1	Documentation

It is recommended that all documentation, including drawings, should be provided before the equipment is commissioned and accepted for the operational purposes. Sufficient copies will be required for the base, outstations and maintenance personnel.

The documentation should include the following:-

- Functional description.

- Technical specifications.

- Lay out diagrams.

- Circuit drawings.

- Assembly drawings.

- Wiring diagrams.

- Installation drawings.

- Configuration software.

- Operating and functional procedures.

- Repair procedures.

- Test procedures.

- Test sheets.

- Acceptance procedures.

- Acceptance test sheet.

## 11.2	Training

Training should be provided to match the sophistication of the system and the skills of the staff involved in the operation and maintenance of the system.  Such training should be scheduled to match the implementation programme and should be defined in the light of what the trainee shall be able to do at the end of the period of training.  Simple systems will require less training, for example, electro-mechanical systems.  Larger computer based systems will require a wider range of training modules as detailed below:

- Operational knowledge of the monitoring and control equipment.

- Principal of the operation and control of outstation equipment.

- Maintenance and repairs of outstation hardware.

- Configuration of outstation software.

- Configuration of base station database and displays.

- Configuration of base station system software.

- System architecture.

Training modules should be selected to suit the operational and maintenance philosophy of the authority and the needs of the staff.

# 12.	FUTURE DEVELOPMENT

## 12.1	General

Techniques and devices used for Remote Monitoring and Control Systems are constantly under review and development by the manufacturing industry which can lead to reduced equipment costs and improvements in reliability. These advances in technology however do not mean that systems need to be replaced on a regular basis, but only when a clear advantage can be predicted or demonstrated. There are numerous cases where equipment installed 10 to 15 years ago is still working satisfactorily. When a new remote monitoring and control system is acquired, the Purchaser and Supplier will usually define a “working life” for the system, at time of purchase.

As more AtoNs are fitted with AtoN AIS it is likely that many authorities will monitor these via AIS if they have access to a Base Station network with appropriate coverage and data processing.

## 12.2	Developments

It is anticipated that development will take place in the field of Remote Monitoring and Control and Communications. The following suggestions are put forward for consideration:

12.2.1	Energy Consumption

The introduction of more efficient semiconductors and processors, that reduce power supply  requirements and enable the use of Monitoring and/or Monitoring and Control Systems where previously  power supply restrictions prevented their use, eg. photovoltaic solar powered stations, buoys.

12.2.2	Signal Formats

The introduction of combined navigation equipment and monitoring and control equipment will require Authorities to agree to common signal format standards.

12.2.3	Communications

New techniques for communication channels providing greater functionality and reliability using systems such as cellular GSM, direct satellite links, Internet, global mobile personal communications by satellite (GMPCS) and low energy consumption radio links.

12.2.4	Radio Navigation

Introduction of a new and updated World Wide Radionavigation System to provide improved accuracy data and integrity facilitating monitoring the position of floating aids to navigation.

The growing dependence of mariners on radio navigation systems, such as DGPS necessitate high integrity RMC systems.  This may imply an availability requirement for RMC exceeding that of the AtoN.

12.2.5	Costs

Developments in remote monitoring and control equipment are likely to offer lower system costs, reduced energy consumption and greater  reliability.