EEP12/6/12

AISM Association of Internationale de Signalisation Maritime  IALA

International Association of Marine Aids to Navigation and Lighthouse Authorities

IALABATT WG 1

2008 -10- 02

IALA Guideline No. 1042-0

On

Selection of Power Systems for Aids to Navigation and Associated Equipment

Edition 1

October 2008

(Replaces IALA Guidelines on Power Sources for Aids to navigation, December 2004)

20ter, rue Schnapper, 78100

Saint Germain en Laye, France

Telephone +33 1 34 51 70 0 Telefax +33 1 34 51 82 05

E-mail - iala-aism@wanadoo.fr      		Internet -  http://iala-aism.org

Table of contents

1	Introduction	3

2	How to use this guideline	3

2.1	Scope	3

2.2	Application of the 1042 Guideline	4

3	Selection Of Power Systems And Energy Storage	5

3.1	General	5

3.2	Guidance on Power Sources	5

3.3	User Requirements	8

3.4	Automation	8

4	Life Cycle Management Considerations	8

4.1	Initiation phase	8

4.2	Implementation and In-Service phases	9

4.3	Disposal phase	9

5	References	10

6	IALA Related Documents	10

6.1	Relevant IEC Standards	11

Annex 1 - Solar Photovoltaic Glossary	12

Annex 2 - Results of the Year 2000 Survey of the Use of PV Energy Systems by IALA Members	15

1	Respondents	15

2	Summary of Main Conclusions	15

2.1	Tabular Summary – Load	16

2.2	Tabular Summary – Batteries	17

2.3	Tabular Summary - Typical Solar Generator Sizes	17

# Introduction

The purpose of this Guideline is to assist Authorities in the selection and design of power systems for Aids to Navigation (AtoN),.

This guideline contains descriptions of power generation, energy storage, load identification and calculation methodologies that are available for use with AtoN, together with their advantages and disadvantages.

Suggestions on Life Cycle Management issues are also addressed in the document.

# How to use this guideline

This document is an overarching guideline and needs to be read in conjunction with the following documents:

IALA Guideline 1042-1 Power/Load Calculation

IALA Guideline 1042-2 Power Generation Energy Storage

IALA Guideline 1042-3 Energy Storage

## Scope

This guideline is focused on delivery of power systems but may equally be applied to ancillary services such as security systems, remote control, monitoring and domestic loads.

The following flowchart shows the steps needed to make the best use of this guideline.

## Application of the 1042 Guideline

hg

# Selection Of Power Systems And Energy Storage

This section identifies those items that should be taken into consideration when selecting energy storage and associated power systems for AtoN  locations.  Table 1 provides general guidance on the most appropriate power systems for a number of locations, power requirements and environmental issues. However, it would be prudent to use the appropriate guideline to better determine the potential and define the optimal solution.

## General

The power requirement for AtoN cannot be based on the light source in isolation because the power system provides for the total needs of the AtoN.  This may include fog signals, lights, racons, remote control and monitoring facilities, security and domestic loads.  Domestic loads can vary substantially - demand on manned stations will be at a constant high level, while the demand on unmanned stations would only occur during routine maintenance visits.

In addition to the development of new light sources, the automation of lighthouses and systems and changing user requirements play a significant part in the relevance and size of power supplies.

However, developments in technology have made it possible to reduce the power consumption of AtoN without any detrimental effect on the service provided to mariners.  In particular, battery systems rather than diesel generators can be used as back up for mains power or as the companion of renewable energy sources. Self contained LED lanterns may also meet the requirements, thus eliminating the need for external power generation and energy storage.

## Guidance on Power Sources

Where power is supplied by others, reliable and readily available, this may be the cheapest energy source. When utility power is used, it is sufficient to provide back-up facilities by means of energy storage solutions.  The capacity of the device need only be sufficient to enable time for access to site and repair.

Where externally supplied power is difficult or impossible to install, solar energy or other renewable source of energy should be considered as the next option. In situations of light loads where solar power is not practicable, primary batteries can be used.

Diesel generators should only be considered for major loads.

Table 1 provides information on the practical choice of energy storage systems and guidance on the application of power sources for aids to navigation.

|  |  |  |  | TABLE 1 |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Selection Guide of power systems |  |  |  |  |  |  |  |  |  |  |  |  |  |
| Power Systems | Remote Site | No Easy Access | High Power > 300 Wh / day | Medium Power 300 - 100 Wh / day | Low Power < 100 Wh / day |  | Extreme Temper- atures | Ventilation not possible |  | Buoy | Major Floating Aid |  | Life Expectancy (estimated years) |
| Mains power | +o | + | ++ | ++ | + |  | ++ | ++ |  | - | - |  | - |
| Diesel generator | + | o | + | - | - |  | o | o |  | - | - |  | 20 |
| Solar | ++ | ++ | - | + | ++ |  | ++ | - |  | ++ | ++ |  | 20 |
| Wind HAWG | ++ | - | o | + | + |  | o | - |  | o | o |  | 1 to 15 |
| Wind VAWG | ++ | - | + | ++ | ++ |  | ++ | - |  | o | + |  | 10 to 50 |
| Fuel Cell | ++ | - | + | ++ | ++ |  | - | o |  | - | - |  | 15 |
| Hybrid | ++ | ++ | o | ++ | + |  | + | o |  | ++ | ++ |  | Not applied |

|  |  |  |  | TABLE 2 |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Selection Guide of energy storage equipment |  |  |  |  |  |  |  |  |  |  |

| Energy Storage | Remote Site | No Easy Access | High Power > 300 Wh / day | Medium Power 300 - 100 Wh / day | Low Power < 100 Wh / day | Extreme Temper- atures | Ventilation not possible | Buoy |  | Major Floating Aid | Life Expectancy (years)/cycles |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
| Lead acid | + | + | + | + | + | - | - | o |  | + |  |
| Sealed lead acid | ++ | o | - | o | + | - | - | ++ |  | + |  |
| VRLA | + | o | o | + | + | - | - | o |  | - |  |
| Pocket NiCd | ++ | o | + | + | + | + | - | o |  | + |  |
| Sintered NiCd | + | o | + | + | + | + | - | o |  | + |  |
| Sealed NiCd | ++ | o | + | + | + | + | - | ++ |  | + |  |
| Air depolarized | o | o | - | - | + | o | - | + |  | o |  |
| Alkaline | o | o | - | - | + | o | ++ | + |  | o |  |
| Zinc-Carbon | - | o | - | - | + | - | ++ | + |  | - |  |
| Ni-MetalHydride | + | o | + | + | + | - | - | + |  | + |  |
| Lithium | + | o | + | + | + | - | - | + |  | + |  |
| Super Capacitor |  |  |  |  |  |  |  |  |  |  |  |
| ++ | Recommended solution |  |  | +o | Recommended solution where mains power is available |  |  |  |  |  |  |
| + | Good solution |  |  | o | Not recommended |  |  |  | - | No comment |  |

## User Requirements

The user requirement also has an important part to play in power consumption.  For every mile reduction in range for lights the required luminous intensity is roughly halved and hence power consumption reduced.  The application of visual and audible AtoNs is changing, ranges are being reduced considerably, resulting in far less power demand.

## Automation

Automation takes away the constant domestic element but may introduces control devices to ensure equipment is on when required, and the converse being that the same device will also switch off the AtoN when not required, thus saving power.  Typical examples are day/night sensing for the light sources, fog detectors for fog signals and state of charge sensors for diesel generators.

### Disadvantages

The continual reduction of power consumption and thus the requirement for smaller power supplies has distinct advantages, but where this is applied to buildings that were originally occupied, there are disadvantages that should be recognised and addressed.

Such buildings had facilities for heating to levels comfortable to the keepers.  With automation, if the level of power available was based only on the consumption needed to operate the AtoNs, there would be no spare capacity for the protection of the fabric of the building.  This may result in damp conditions leading to the deterioration of the building itself as well as the AtoN equipment.

Where mains power is available heating or dehumidification can be provided without increasing the back up power supply.   However, with renewable energy or hybrid operated systems there is no spare capacity for building conditioning, as this would defeat the savings made.  In these cases alternatives need to be considered including:

- Improved ventilation.

- Good building maintenance.

- Ancillary powered heating either by high efficiency gas or diesel fired boilers, solar or wind generators.

- High efficiency Stirling cycle engine to provide heating as well as electrical power.

|  |  | TABLE 3 – Recommended energy source for Aids to Navigation sited at various latitudes |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Required energy/day | Latitude Degrees |  |  |  |  |  |  |

# Life Cycle Management Considerations

The Life Cycle Management covers from conception to disposal and is having an increasing impact on the design and selection of equipment and has also a direct link to the overall financial requirements.

Initiation phase

### Capturing the Mariners Requirements

The start of any AtoN project is that a requirement is identified by a maritime entity. This could range from a vague idea to a thoroughly considered approach. When developing the design criteria for the final solution, it is imperative to achieve full and concise design requirements from the initiating body.

### Consideration of Design Options

Careful consideration should be given to the “Through Life Costs” of any solution as a low capital cost solution could offer very high running costs and visa versa.

It is therefore important to consider the true overall cost of “Ownership” of the AtoN. This consideration should take into account such issues as maintenance periods, equipment replacement periods, and environmental implications, both through life and at end of life disposal. End of life recycling / disposal costs should also be considered.

It should also be noted that in some areas an acceptable solution may be to use lower-priced bateries and accept that their replacement may be necessary more frequently than for specialist batteries.  Such a decision will be influenced by the cost of accessing the AtoN site, and by the ease of fast access in the event of a failure.

### Heritage

With certain AtoN refurbishment or replacement projects, heritage issue may become a consideration. The costs of replacing an “Artefact” piece of equipment cannot be overlooked. These costs are not only monetary, but could be deemed to be a cost on history and could be ignored to the projects detriment. Consideration therefore should be given to the re-use in the new project or leaving the redundant equipment “In situ” for others to see, or relocation of the artefact to a museum or similar place. In any case the cost of any solution should include for this.

### Design life

To enable a final solution to be defined and agreed by the initiating entity a clear view should be available to them that encompasses all the initial criteria, or at least offers them options for consideration.

## Implementation and In-Service phases

During the in-service life of the AtoN equipment, it is important to monitor the performance of the equipment to ensure the protection of the environment.  Appropriate measures should be taken to limit the impact of the maintenance activities on the environment.

Maintenance activities should be appropriate to protect the heritage status of the sites and be compliant with the current regulation, where applicable.

It is recommended that the maintenance requirements be evaluated during the conception phase in a manner to extend the maintenance interval wherever possible.

## Disposal phase

The disposal of any equipment has to be considered during the conception phase in order to minimize the impact on the environment.

Disposal of equipment containing hazardous materials is an increasingly important factor and the emphasis must be put on reworking/reusing components to extend life and then the re-cycling of equipment in preference to disposal. Disposal of non-reusable equipments or components should be limited to the minimum.

It is important to ensure that any disposal of AtoN equipment is done according to current regulations and limits the negative impact on the environment as much as possible.

Consideration should be given to passing on obsolete equipment to a museum, if it might be interest to future generations.

# References

# IALA Related Documents

- Recommendation for the notation of luminous intensity and range of light.   November, 1966.

- Recommendation for a definition of the nominal daytime range of maritime signal lights intended for the guidance of shipping by day.   April 1974.

- Recommendation for the colours of light signals on Aids to Navigation.  December 1977.

- Recommendation on the determination of the luminous intensity of a marine Aid to Navigation light.  December 1977.

- Recommendation for the calculation of the effective intensity of a rhythmic light.  November 1980.

- Recommendation E-110, for the rhythmic characters of lights on Aids to Navigation.  May 1998.

- Recommendation E-112, for leading lights.  May 1998.

- Recommendation E-123, on the Photometry of Marine Aids-to-Navigation Signal Lights.  June 2001.

- Recommendation A-126 on the use of AIS in Aids to Navigation.  December 2003

- IALA practical notes on the application of solar power systems for Aids to Navigation. September 1993.

- Guidelines no. 1012 for the protection of lighthouses and Aids to Navigation against damage from lightning.  December 2000.

- Guidelines no. 1011 on a standard method for defining and calculating the load profile of Aids to Navigation.  December 1999.

- Guidelines no. 1025 on maintenance and operation of batteries.  December 2001.

- Guidelines 1021 on new light sources and associated power supplies. December 2001 (revoked by IALA Guideline no. 1043 December 2004).

- Guidelines No. 1039 on Designing Solar Power Systems for Aids to Navigation (December 2004)

## Relevant IEC Standards

### Battery related

| Standard | Status | Title |
| --- | --- | --- |
| IEC 62060 | Draft | Guide for the use of monitoring systems for lead-acid batteries. |
| IEC 61427 | Issued | Secondary cells and batteries for solar photovoltaic energy systems - General requirements and methods of test. |
| IEC 60896 | Draft | Stationary lead acid batteries - Part 21: Valve regulated types - Functional characteristics and method of test. |

### Solar PV related

| Standard | Status | Title |
| --- | --- | --- |
| IEC 62253 | New work | Photovoltaic stand-alone systems - Design Qualification and Type Approval. |
| IEC 62111 Now renumbered as 62257 Parts 1-10 | Draft | General directive for the use of renewable energies (REN) in decentralised and rural electrification - Rules on the design and operation systems - Architecture of electrification system using PV modules. |
| IEC 62109 | Draft | Electrical safety of static inverters and charge controllers used in photovoltaic power systems. |
| IEC 61427 | Issued | Secondary cells and batteries for solar photovoltaic energy systems. |
| IEC 61683 | Issued | Photovoltaic systems - power conditioners - procedure for measuring efficiency. |
| IEC 61836-2 | New work | Specification for the use of renewable energies in rural decentralised electrification. |

Annex 1 - Solar Photovoltaic Glossary

Note that the terms relating to the solar photovoltaic part of the system are extracted from IEC TC 82 “Solar photovoltaic energy systems Guide: Glossary of terms and symbols used in solar photovoltaic energy systems - part I - 82/154”.

Attention is drawn to the IALA Dictionary, chapter 6, Power Supplies for Stations. Section 2, Natural Energy Sources and Low Level Sources. Also Section 4 Electrochemical Cells and Batteries.

Array:

A mechanically integrated assembly of modules or panels together with support structure but exclusive of foundation, tracking, thermal control and other such components, to form a DC power producing unit.

Autonomy of a Battery:

The autonomy of a battery is a theoretical concept. It indicates the time in days (or hours) a battery will take to discharge from a fully charged state [100 % state of charge (SOC)] to a chosen cut-off level state of charge, powering the AtoN system without any energy coming from the generator.

The cut-off level is chosen by the designer according to the battery technology used.

It should be noted that the electrical power consumed by the AtoN system (in Ah/day or Wh/day) may vary with weather conditions and/or season of the year. It is recommended to use the worst conditions (night duration & temperature) to calculate the battery autonomy.

Battery state of charge

Time

100%

0%

Cut-off level

Autonomy

Conversion efficiency:

The ratio of maximum electrical power output to the product of photovoltaic device area and incident irradiance measured under defined test conditions and expressed as a percentage.

Current-voltage characteristics (I = f (V)):

The output current of a photovoltaic device as a function of output voltage at a particular temperature and irradiance.

Fill Factor (FF) :

The ratio of maximum power to the product of open-circuit voltage and short-circuit current

FF=PmaxVoc∗Isc

Irradiance:

(Wm־²) radiant power incident upon unit area of surface.

Irradiance, Direct (Wmֿ²):

The radiant power from the sun's disc and from a small circumsolar region of the sky within a subtended angle of 5º incident upon unit area.

Irradiance, Diffuse: (Wmֿ²):

The total radiant power incident upon a unit area excluding the direct irradiance.

Irradiation :

Integration of irradiance over a specified period of time. (MJm־² per hour, day, week, month, year, as the case may be).

Module:

The smallest complete environmentally protected assembly of cells.

Module area:

The entire frontal area of the module, including borders and frame (m²).

Module packaging efficiency:

The ratio of the total cell area to module area.

Panel :

A group of modules fastened together, pre-assembled and wired, designed to serve as an installable unit in an array and/or sub-array.

Panel area (m²):

The entire frontal area of the panel, including modules, inter-module framework and spacing.

Panel packing efficiency:

The ratio of the total module area to panel area.

Photovoltaic effect:

Direct conversion of radiant energy into electrical energy.

Photovoltaic (PV) System:

An installed aggregate of components and subsystems that combine to use the photovoltaic effect to convert solar energy into electrical energy suitable for connection to an application load. In its simplest form a PV system consists of a PV array with connections to the load, but it may also include power conditioning, monitoring and control equipment, energy storage and power distribution units.

Rated current:

The measured value of current of a PV device at rated voltage under Specified Operating Conditions.

Rated maximum power:

The value of maximum power of a photovoltaic device under Specified Operating Conditions.

Rated power:

The value of power output of a photovoltaic device at rated voltage under Specified Operating Conditions.

Rated voltage:

The voltage at which a PV device is designed to produce near maximum electrical power under Specified Operating Conditions.

Reference solar cell:

A solar cell used to measure irradiance or to set simulator irradiance levels in terms of a reference solar spectral irradiance distribution.

Short circuit current (Isc):

The output current of a photovoltaic device in the short-circuit condition at a particular temperature and irradiance.

Solar cell:

The basic photovoltaic device that generates electricity when exposed to sunlight.

Solar cell area:

The entire frontal area of the solar cell, including the cell grid (cm²).

Spectral response (absolute) (S abs):

The short circuit current density generated by unit irradiance at a particular wavelength (AW־¹), plotted as a function of wavelength.

Spectral response (relative) (S rel):

The spectral response normalised to unity at wavelength of maximum response.

Voltage temperature coefficient:

The change of the open circuit voltage of a PV device per degree Celsius change of cell temperature.

This coefficient varies with irradiance and to a lesser extent with temperature.

Annex 2 - Results of the Year 2000 Survey of the Use of PV Energy Systems by IALA Members

During the year 2000, IALA sought information from its members via a questionnaire on energy sources, with the objective of generating some statistics relating to the use of various energy sources for AtoN, particularly PV energy sources.

# Respondents

The countries which answered the inquiry covered all latitudes from 0° to 80° North and South and represented operators of:

- 30,425 floating AtoNs and

- 44,044 fixed AtoNs.

Readers should also remember that despite the reasonably large numbers of respondents to the questionnaire in 2000, the results are necessarily affected by some authorities having large numbers of AtoN in service compared with the numbers of other authorities. Note that the results are analysed by numbers of AtoN, not by numbers of Authorities.

# Summary of Main Conclusions

As a result of an analysis of the returned questionnaires, it appears that in 2000, for the AtoN operated by the respondents to the survey:

- 49% of fixed AtoNs and 30.6% of floating AtoNs were powered by solar PV systems.

- 12.6% of fixed AtoNs were powered from the public utilities supply.

- 3.3% of fixed AtoNs and 8.2% of floating AtoNs were powered by primary cells (not rechargeable) mainly in the countries operating floating AtoN above 60' latitude.

- 1.2% of fixed AtoNs and 2.3% of floating AtoNs were powered by gas (mainly acetylene).

- 1.2% of fixed AtoNs were powered by diesel generators.

- 0.1% of fixed AtoNs were powered by kerosene.

- 0.3% of fixed AtoNs and none of the floating AtoNs were powered by wind-powered generator.

- Only a tiny number of AtoN utilised wave, seawater battery or other unusual power sources.

- Very few fixed AtoN had hybrid sources. These were mainly solar PV with diesel generator back-up and very occasionally also with wind back-up. Some were PV with wind back-up.

- A small number (less than I %) of floating AtoN had hybrid sources mainly PV and wave, or PV and primary cells.

## Tabular Summary – Load

Analysis of the survey information showed that the averaged load values were as follows.

| Parameters | Fixed |  |  | Floating |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | Min | Typical | Max | Min | Typical | Max |
| Average power of the load (Watt) | 3 | 21 | 50 | 3 | 10 | 22 |
| Max. power of the load (Watt) | 5 | 181 | 1000 | 5 | 25 | 100 |
| Min. power of the load (Watt) | 1.5 | 7 | 20 | 2 | 7 | 10 |
| Average duty cycle | 0.1 | 0.2 | 0.5 | 0.1 | 0.21 | 0.5 |

Average power of the load: Σ (P lamp x duty cycle) / total number of AtoN under consideration.

Average duty cycle: Σ (duty cycle) / total number of AtoN under consideration

## Tabular Summary – Batteries

Analysis of the survey information showed that the averaged battery capacities were as follows.

| Parameters Average capacity (Ah) | Fixed |  |  | Floating |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | Min | Typical | Max | Min | Typical | Max |
|  | 100 | 310 | 500 | 100 | 285 | 1000 |
| Technology | Lead-acid flooded preferred (56%) |  |  | VRLA preferred (81%) generally gelled electrolyte except for freezing sites. |  |  |
| Average autonomy without solar production in days | 4 | 30 | 120 | 10 | 45 | 90 |
| Battery conditioning |  |  |  | Generally vented container in buoy superstructure (30 %) |  |  |
| Average duration life in years at 75% of nominal capacity at the end of life | 4 | 9 | 20 | 3 | 5 | 10 |

## Tabular Summary - Typical Solar Generator Sizes

The results, covering a total of 840 kWp installed module power, showed the following for the averaged peak Watts figure for the PV generator.

|  | Fixed |  |  | Floating |  |  |
| --- | --- | --- | --- | --- | --- | --- |
|  | Min | Typical | Max | Min | Typical | Max |
| Average power per AtoN (Wp) | 20 | 186 | 833 | 20 | 89 | 300 |
| Largest generator (Wp) | 100 | 1495 | 4400 | 30 | 256 | 3500 |
| Smallest generator (Wp) | 3 | 22 | 48 | 3 | 41 | 300 |
| Peak power of the generally used modules (Wp) | 10 | 50 | 80 | 10 | 50 | 80 |
| Tilting angle | Latitude + 15° |  |  | Generally more than 60º (sometimes horizontal) |  |  |