IALABATT WG-1

2008-10-02

IALA Guideline No. 1042-22

On

Energy Storage for Aids to NavigationPower Sources

Edition 10

October 2008

AISM Association of Internationale de Signalisation Maritime  IALA

International Association of Marine Aids to Navigation and Lighthouse Authorities

20ter, rue Schnapper, 78100

Saint Germain en Laye, France

Telephone +33 1 34 51 70 0 Telefax +33 1 34 51 82 05

E-mail - iala-aism@wanadoo.fr      		Internet -  www.iala-aism.org

Document Revisions

Revisions to the IALA Document are to be noted in the table prior to the issue of a revised document.

| Date | Page / Section Revised | Requirement for Revision |
| --- | --- | --- |

TABLE OF CONTENTS

1	INTRODUCTION	4

1.1	Scope and purpose	4

1.2	Types of battery power systems	4

1.3	Categories for Application of Secondary Batteries	5

2	MAJOR ADVANTAGES AND DISADVANTAGES OF VARIOUS TYPES OF BATTERIES USED IN MARINE ATON	5

2.1	Existing Battery Types	5

2.2	New Battery Types	9

3	OPERATIONAL CRITERIA FOR SECONDARY BATTERIES FOR PHOTOVOLTAIC APPLICATIONS	10

3.1	General operating conditions	10

3.2	Capacity	14

3.3	Cycle Life	14

3.4	Charge control	14

3.5	Charge retention	15

3.6	Over discharge protection	15

3.7	Mechanical endurance	15

3.8	Recycling and Disposal	16

4	SAFE HANDLING OF BATTERIES	16

4.1	Battery Safety Issues	16

4.2	Installation	17

4.3	Ventilation	17

5	MAINTENANCE PRACTICES	20

5.1	General considerations	20

5.2	Inspections	21

5.3	Tests	23

5.4	Faults	23

5.5	Corrective Actions - General	23

5.6	Remote Monitoring	25

# AC MAINS POWER

The availability of AC mains power at or near the site should be one of the first considerations.

Advantages:

- Load on the system is not critical.

- Relatively low cost.

- Low maintenance.

Disadvantages:

- Possible unreliability of the AC power supply.

- Addition of a back up system that will need periodic maintenance.

Comment:

- Interference from lightning strikes is a possibility that should be considered.  IALA Guidelines on Protection of Lighthouses and AtoN against Damage from Lightning, June 2000, refer.

# PHOTOVOLTAIC POWER

## INTRODUCTION TO PHOTOVOLTAIC (PV) SYSTEMS

More than 50% of AtoN are powered using PV systems and the trend is for increasing usage.

The approach taken in sizing the PV power systems may be different in different parts of the world. For a given load or site there is no one correct design solution. For example, increasing the area of PV modules and decreasing battery size may be possible and vice versa.

An AtoN PV power system, in its simplest form, consists of a solar panel and a secondary battery. A charge regulator may also be used. PV power systems are a well-proven technology and equipment is available from many suppliers. When properly designed with due consideration for protection from the marine environment, PV power systems are very reliable and are the most widely used renewable energy source for charging secondary batteries.

## Conversion of Existing Lights to PV Energy

There has been a trend in some countries to reduce the range of long-range visual AtoN.  This, combined with the use of modern high efficiency light sources, may mean that the AtoN can be converted to PV energy.

## PV Module Technology

The most commonly used technologies are single crystalline or multi-crystalline silicon solar cells encapsulated with glass in front and glass, resin, tedlar, or metal backing. Amorphous silicon PV modules are less efficient, have progressive reduction in power output with a lower life expectancy, and therefore, are not generally recommended for AtoN applications.

All single crystalline or multi-crystalline technologies are the subject of continuing research driven by grid connection systems, leading to reduction in cost. Marine modules are, however, produced in smaller quantities with attention paid to the specialised environmental packaging.

From a life cycle management point of view, this is of benefit in providing the required level of service.

### Modular Design Considerations

If the installation consists of a single AtoN, it is usually matched to a single power unit, which normally comprises of one or more solar PV modules, a battery and a charge regulator.

If the installation consists of more than one AtoN, or a combination of AtoNs and control systems, the choice lies between having separate power systems for each system load or a solar PV power system that feeds a common supply bus bar.

The use of a separate power system for each AtoN has the advantage that if the power to one AtoN fails, the other AtoNs will continue to operate normally, but such a system will have a higher initial cost, and will require slightly more time for maintenance visits.

The common supply power system may have advantages in allowing a closer match between the power system and the total station load, but would require protection against over-consumption or short circuits in any of the loads.

If the equipment that is used at the station requires several operating voltages, this may dictate the number of power systems to be installed. The final choice of system configuration lies in a careful evaluation of the advantages and disadvantages of the possible configurations used to meet the operational availability.

### Example of a Modular Design Concept

The Australian Maritime Safety Authority has implemented the following concept:  Use of a standardised solar PV powered generator (module + battery + charge regulator) that is installed in multiples to reach the power needed or to increase the reliability.

Secondary Energy Sources

A cost comparison between A) - over sizing the PV generator and B) - adding a secondary energy source should be made, taking into account the fact that, generally, back up sources are less reliable than solar PV generators. However, with large PV generators (> 1000 Wp) and at latitudes above 40° where summer and winter solar irradiation levels are quite different, a secondary source can be considered for the purpose of reducing the system battery capacity, at the same time saving weight, equipment volume and building space. Portable generators have been used to minimise life cycle costs by including the charge during scheduled maintenance.

## Solar Sizing Design Computer Programs

Computer programs allow for many inter-related factors including statistical insolation throughout the year, land and sea reflection coefficients, temperature variations, PV array tilt angle, PV module and battery efficiencies, battery self-discharge, battery electrolyte temperature and accurate electrical load profile. These programs should take account of these factors for each period of the year [typically every month].  Many such programs contain a database of solar insolation data for a large number of global locations.

Some programmes may be pre-loaded with defined solar module and battery characteristics. Less sophisticated programmes may require the operator to interpret the programme output by selecting numbers and ratings of batteries and modules.

A detailed knowledge of the solar insolation data for a given site is a primary requirement for accurate system design. Various organisations have gathered insolation data that may be relevant for the area in question.

It is important to compare conditions at sites where published data has been obtained with those at the installation site. Local cloud or mist conditions and local topography may considerably affect coastal sites by shading the solar array. Vegetation at land sites may mean that the solar energy input is less than the programme might predict. Allowance may have to be made for sand, dust, or industrial deposits on the solar array.

The problems associated with array sizing increase in the higher latitudes, because variations of energy production and consumption are greater.añadir mencion latitudes >65 deg

Some of the authorities having their own in-house solar sizing programmes are willing to make their programmes available to IALA members, free of charge, but language, and introduction of specific solar data can be obstacles to their use by others.

Some AtoN manufacturers and some solar module manufacturers will carry out computer design of solar power systems.

The IALA program on Designing Solar Power Systems for Aids to Navigation (Dec. 2004) refer.

NOTE: The IALA Software calculation excel program  provides an iterative method of designing a solar power system for fixed or floating AtoN installations.

To obtain the excel program, including password and manual (previous guideline 1039) please contact IALA Secretariat via e-mail:  iala-aism@wanadoo.fr

### Integrated power system lanterns.

It is not possible to have the same light intensity using the same solar system throughout the world.

Consideration should be given to asking the supplier to state the operational life expectancy and expected reliability and performance under the specified design conditions over an identified time period, typically three to five years.

Users should specify their operational requirements as under low battery voltage conditions, the light may turn off completely or reduce its intensity pro rata with battery charging data.

Area specific solar data is required to properly size the solar PV system for a self contained light. The ability to deliver the required range taking account of vertical divergence and flash character to the required operating standard depends on the specific data for the site. In addition, consideration should be given to the assumptions made for the battery autonomy requirements. Degradation in the performance of the battery should also be considered for the stated life span of the unit.

The installer of the lantern should also take into account the site topography to minimise shading of the solar array.

### PV Energy on Buoys

Sizing the solar power system on a buoy is subject to greater variations than one on a fixed structure.  Some programmes may include rough rules-of-thumb to account for buoy movement and alignment, however experience in the use of solar power systems on buoys is also important. When choosing a programme to use for solar system design, authorities should be aware of what rules are being applied by that programme.

## Batteries for PV Energy Systems

A good starting point when sizing a system is to base the battery Ah capacity on the autonomy required (autonomy being the time the designer wishes the equipment to continue to perform under "no sun" condition – Annex 1 – Terminology - refers).

### Computing the Capacity Needed

The required battery capacity is typically calculated by multiplying the maximum daily load in amp-hours/day, by the desired hours (days) of autonomy, divided by the lowest intended state of charge according to the battery technology used (> 0.3), and finally multiplying by a safety factor (around 1.3), which allows for capacity loss during the operational life of the battery, resistive losses, etc.  This calculation is of course automatically done by PV system software.

### Temperature Effects.

Note that effective battery capacity will be significantly reduced (by as much as 50%) by high (above 40ºC) or low (below - 5ºC) battery temperature. In hot or cold climates special precautions should be taken to protect batteries from excessive temperature, and battery manufacturers and the customer should acknowledge the operating temperature for the type of battery under consideration. High temperature conditions will have an impact on life expectancy.

### Minimum and Maximum Capacity

The minimum battery capacity will depend on the choice made or imposed for the following design constraints:

- Maximum daily depth of discharge.

- Lowest acceptable level of charge during the winter months.

- Allowance for “no sun” days (from meteorological or insolation data). According to the inquiry, 20 days minimum is a rule of thumb for medium latitude (less in lower latitudes and more in higher ones).

- Ease of access to the AtoN.

- Ability of the battery to accept the peak output of the generator without overcharging, mainly for sealed batteries (a situation that may arise with a self-regulating system).

It should be noted that:

- The maximum battery capacity will usually be determined by consideration of cost, available space, weight, and handling capacity. As a general rule the number of batteries in parallel should be kept to a minimum. (Five is a typical figure for good quality batteries coming from the same production batch, installed at the same time and working under the same regime of charge and discharge. It could vary according to the quality of the battery). Some manufacturers offer individual cells or blocks of 2 or 3 cells, with high Ah capacity, and it is usually better to use these in series rather than to parallel smaller batteries.

- Use of lead-acid batteries may require an increase in battery capacity to prevent deep discharge during winter months, but in this situation the effect of low temperature on the battery should be taken into account. For these reasons nickel-cadmium, nickel metal hydride and lithium ion batteries should be considered for the worst cases (very high latitude in the northern and southern hemispheres and very low temperature).

- Batteries with low self–discharge become important when the design requires a long autonomous period for the system.

### Batteries on Buoys

The expected battery life on buoys can be shorter than for a land station, due to shock-load damage of the plates especially for flooded batteries.

AGM and gelled electrolyte batteries are often used on buoys to prevent spillage of electrolyte. Consult with the manufacturer.

### Advances in Technology

Battery manufacturers or suppliers should be consulted during AtoN system design, as battery technology is continually evolving.

### Quality Versus Price

It should also be noted that in some areas an acceptable solution may be to use lower-priced batteries and accept that their replacement may be necessary more frequently than for specialist batteries. Such a decision will be influenced by the costs of accessing the AtoN site, and by the ease of fast access in the event of a failure.

### Battery Maintenance

Refer to IALA Guidelines on Battery Maintenance Guidelines no. 1025 on maintenance and operation of batteries.  December 2001.  It is important to note that ventilation is required when all types of secondary batteries are being charged.

Even very small solar installations can overcharge a battery given a suitable combination of circumstances. Sealed batteries of all types have some form of a pressure vent and if overcharged they will generate hydrogen in potentially explosive proportions. All battery housings, including buoys, must be effectively ventilated and free from ignition sources.

Safe working practices must be established for opening battery boxes or compartments.

### Charge Regulation

A high charge efficiency is needed so that most of the energy produced by the PV array is stored in the battery.  A modern electronic charge regulator will generally ensure this.

There are three possibilities for the charge regime:

#### No Charge Regulator and Conventional PV Module

- Mainly for low latitude and nickel-cadmium batteries.

- A lack of a regulator can mean periodical overcharge and gassing of the battery, necessitating frequent topping up with water. This design is not recommended.

#### Self-regulated PV Modules

- Usually these are modules with only 32 solar cells or less for 12V systems, to match the required charging voltage to the battery.

- With self-regulation the battery capacity may need to be increased to prevent frequent overcharging.

- With VRLA batteries, the charge rate should not exceed about 1 ampere per 100 amp-hours capacity (C/100 charge rate).

- In hot climates the use of VRLA batteries with self-regulated modules should be avoided.

- The major advantage of using self-regulated PV modules [no charge regulator] is maximum simplicity. In practice the battery is generally not working in the best conditions and its life will be shortened, so that more frequent battery replacement will be needed.

#### Electronic Charge Regulator

- Can be either series or parallel type to protect against overcharge or complete discharge.

- The advantage of shunt regulation is low component count and low self-consumption.

- All regulators require some cooling.

- Prolongs the battery life and reduces the need for topping up.

- Ensures that the battery is operated within its designed operating specifications.

- With a series regulator there is only small energy dissipation.

- Lithium ion batteries require a specific type of regulator incorporated in the battery pack.

- Generally charge regulators have a long Mean Time Between Failures [MTBF].  Static switching (e.g. MOS FET) charge regulators have a very high level of reliability with very low voltage drop.

### Charging Parameters

For long battery life, the maximum charge voltage should be set to ensure the battery is fully charged for a significant period of time during summer. This adjustment represents a delicate balance between excessive water consumption and the battery never becoming fully charged.

The batteries should be pre-formed (charge cycled approximately three times) prior to installation for maximum battery capacity and life in accordance with the manufacturers recommendations.

For a vented battery, some water consumption, apart from evaporation, between the specified topping up levels over a year's operation can be considered normal.

For a “sealed” battery overcharging can mean a loss of capacity. Battery manufacturers’ recommendations should be accurately followed on this point. Use solar regulators without equalization charge function to prevent overcharging the sealed batteries.

Maximum power tracking where the electronic regulator automatically maximises the charge for any level of insolation can be a useful feature.

The use of a low voltage load disconnect mechanism, or load shedding, is also recommended to prevent premature ageing of the battery and possible failure, which may result from excessive battery discharge.  This feature may be included in the load, for example this feature is included in some AtoN lanterns, so that it can be a part of a simple non-regulated, or self-regulated, solar power system. Electronic charge regulators are also available with this feature.

As many charge regulators are based on the measurement of battery voltage it is very important that the voltage measured by the regulator is not concerned with a voltage drop (loss) due to conductor size or poor connections (locking, corrosion).  Some charge regulators, especially for larger solar systems, are provided with separate terminals for battery voltage sensing, and require that separate cable cores be run to the battery for this purpose.

The charge control regime should take into account the battery temperature, particularly in high and low temperature applications. The voltage level cut-off is generally defined for 25˚C. For instance it should be reduced by a few mV every time the temperature increases by 1˚C. Users should refer to battery manufacturer specifications for the exact value.

NiCd batteries require voltage control during charging adjusted for ambient temperature if low water consumption is wanted.

Nickel Metal Hydride NiMH batteries require voltage control using series regulators.

Lithium Ion and Lithium polymer batteries require special built-in  complex charging control regulator.

For large PV generators (e.g. greater than 1000 Wp), charge controllers with the following features may help to increase efficiency of the charge to the battery:

- Automatic facility to allow for a cell-equalising charge following deep discharge of the battery.

- State of charge indicator connected into the monitoring system.

- Ah or Watt-hour counter.

- Remote monitoring of charging parameters (end-of-charge voltage level, etc).

- The effects of stratification over long period of time should be considered.

### Remote Monitoring of Battery Condition.

Primarily, for large PV installations with significant investment costs, as might be found at lighthouses or major beacons or at installations in high latitudes in both northern and southern hemispheres, remote monitoring and control of the battery parameters can be cost-effective. It allows battery condition to be checked remotely, and remedial action taken as necessary. Sometimes the remedial action may be initiated remotely over the monitoring and control link.

Some regulators are available with a data port output; this is useful for allowing easy connection to a remote monitoring system. Such regulators can provide battery voltage and condition data via the data port.

### Blocking Diodes

A blocking diode is used to prevent undesired discharge current from battery to module(s) or through a shunt regulator.

The blocking diode should be of the low voltage loss type, such as a Schottky diode. It is advisable to use one blocking diode per module because only one module would then be affected by a diode failure.

The switching device in a series regulator can save the blocking diode and corresponding energy loss, but in the case of a failure of the switching device, the battery can partially discharge through the PV module. With a shunt regulator, a blocking diode is essential.

A blocking diode should have a minimum direct current value of three times the short circuit current of the module (array) on which it is installed. The PIV (peak inverse voltage) should be greater than twice the system open circuit voltage.

### Shading (or bypass) Diodes

Above 24V, diodes should be installed to prevent damage when parts of the array are partially shaded.

## Practical Considerations

It should be noted that PV modules that power AtoN are generally placed in locations with difficult environmental conditions, such as:

- Isolated sites, possibly liable to theft or vandalism.

- Sea locations, with wave impact, storms, corrosion, ice, snow, hail, sand abrasion, and lightning.

- Locations where bird fouling and bird attacks are likely.  Birds and animals are known to sometimes attack plastic insulation on cables and plastic encapsulation.

The service life of solar modules can be up to 20 years. Manufacturers commonly offer power output guarantees, and module life guarantees (typically 10 years with maximum 10 % reduction of output power). As with other professional investment decisions, the initial investment costs should be weighed against the costs of maintenance (vehicle, tender, helicopter, and people).

It may be difficult to obtain exact replacement modules in the future as they may be of different dimensions. End users may wish to purchase some spares to cover life cycle management.

### Practical Guide to Choice of Energy Systems

Tables 2 and 3 are intended to assist in the selection of power systems for required types and sizes of loads, however these are only approximate indications.

## Installation of Modules

### Electrical Connections

Some manufacturers supply their modules with waterproof junction boxes attached to the back. For modules with flying leads, care should be taken to properly secure the flying lead, and to ensure that no excessive mechanical load is placed on the lead at the point where it enters the module. Low AWG number equivalent to high csa (mm2) should be used to have reduced resistance and a sufficient mechanical strength. Cables should be suitable for UV and the marine environment. The conductors would be better protected by plating, e.g. tinned copper wire.

### Installation.

Care should be taken at installation to see that the mounting hardware does not stress the module.

Prevention against galvanic corrosion between dissimilar metals (frame/structure) using insulators or stand-offs is recommended.

Care should be taken with total or partial shadowing of the modules during the day or any season. Attention should be paid to growing trees, grass, and other equipment.

Note that shadowing of one cell in a module will cause the output from all the cells in that series string to be partially or totally lost.

Devices (special screws or nuts, welded pieces, etc.) to dissuade thieves from removing the modules are recommended as well as a notice board indicating the importance of the installation for maritime safety.

In areas where theft is a problem, lanterns with integral solar power systems may be desirable.

Remote monitoring is useful to detect intrusion.

### Protection from Bird Fouling

In some areas birds cause real problems by fouling modules. A great number of devices have been devised but none are totally effective, and bird spikes (plastic or metal) are preferred. Devices working at some places don’t work at others. Vertical modules reduce the problem, but imply over sizing. The hazards presented to servicing personnel by metal bird spikes should be considered.

### Mechanical Protection

Protection to reduce the effect of wave impact, storms, vandalism, theft, and buoy-handling, is generally required. Mechanical backing to the module to reduce the effect of wave impact should be so as not to affect the solar cell temperature and hence efficiency. Efficiency versus mechanical strength should be considered.

A shock-absorbing fender may reduce the effect of impact by a workboat.

Vertical mounting of the modules on a floating AtoN reduces the vulnerability of the modules.

Metal backing behind the modules, and a clear front cover over the modules might reduce the effect of vandalism, but generally a front cover affects the efficiency because of lower transmission. This effect will increase if the cover is not self-cleaning or becomes dirty.

Metal backing may protect modules that have resin on the back, from bird pecking.

### Tilt Angle of the Module

For fixed installations, the solar array should face the equator. The modules are generally mounted so that the angle between the module and the horizontal varies from being equal to the latitude angle at low latitudes, to the latitude angle plus 20 degrees at high latitudes. To minimise the effects of bird fouling (even with bird protection) and dirt deposits, it is better not to have horizontal modules and tilting should never be less than 20 degrees.

On floating AtoNs, where the orientation of the modules is random, modules are usually distributed around the vertical axis of the buoy (2 at 180°, 3 at 120° etc). Modules mounted at a steep angle, or even vertically, make automatic washing of salt or bird fouling by rain or sea spray more efficient. This also can make integration in the superstructure easier, and protection from damage more effective. The loss of energy at such mounting angles is partially compensated by reflection from the water surface. Some authorities have a policy of mounting single modules horizontally above the lantern on buoys. The horizontal mounting of modules is not recommended for high latitudes in both the northern and southern hemispheres.

During winter months, at medium latitude (45º±5º) 2 vertical modules produce around 1.5 times more energy than one horizontal module with the same peak power. One vertical module produces 0.7 times the energy of a module which would have been installed so as to have the optimal tilt angle at the worst period.

### Lightning Protection.

It can be said that no protection is better than a bad protection system.

A protected station should have its lightning protection system checked every year.

A current practice is to ground (earth) the metallic frames of all equipment - electric conductors are left floating.

A overvoltage arresters devices will be used to increase the proteccion in the solar charge regulator connections.

On non-metal buoys, an air terminal on the top, directly connected to the mooring chain, can limit damage from lightning.

Refer to the IALA Guideline on protection of Lighthouses and Aids to Navigation against Damage from Lightening, June 2000.

## Maintenance

Maintenance of a PV power system at AtoN should, of course, be planned as part of a total maintenance programme for all components of the AtoN site. Minimum maintenance is required as part of life cycle costs. This is facilitated by initial investment and by selection of the correct systems.

### Programmed Maintenance

For the PV power system, maintenance will probably include some or all of the following:

- Battery top-up as necessary.

- Check state of charge, open-circuit voltage and loaded voltage, and specific gravity and the general condition of the battery. [Measuring of specific gravity applies to flooded Lead Acid batteries only].

- Check external aspect of the battery plates and accumulation of sediment when batteries with transparent cases are used.

- Inspect the PV modules for corrosion [especially at the inter-cell connections and at the output terminals], discoloration of the encapsulant, de-lamination in the borders by ice effects. or bird fouling.

- Confirm load demand is within specified limits.

- Check connections and condition of cables.

- A check should be made for changes in environmental conditions, which may result in shadowing of the PV modules, i.e. trees, new buildings, etc.

- Routine cleaning, and the greasing of battery terminals.

Solar modules should not need maintenance, only inspection and cleaning.

### PV Module Degradation Check

The performance of PV modules may be checked at longer intervals by using a reference solar cell (to test at minimum the short circuit current and the open circuit voltage for each module). To avoid destruction or accident a specialist should do this test.

### Frequency of Maintenance Visits

In many locations, one maintenance visit per year should be adequate for a correctly designed system.  There might be some sites where industrial fall-out, wind-carried sand, or a high bird population requires a more frequent schedule. In some hotter climates it may be better to visit twice per year for battery top-up.

Primarily for large installations two visits per year, especially for a recently installed station, is a good practice:

- One visit in the autumn to ensure the battery is fully charged and the PV array in good condition.

- One visit in the spring to correct any damage after the winter period, to add water to the batteries (if flooded type), and to be sure the array can fully charge the battery during summer.

- After that it should be possible to move to an annual inspection.

With experience, it can be possible to extend inspection periods to one or more years for many installations.

The trend for buoys is for a period of between two to four years (and increasing) with the period being determined by other requirements, e.g. moorings.

### Training Of Maintenance Personnel

A PV system is a crucial part of an AtoN system and the Authority should therefore make sure that the people who service such a system are already been made fully aware of how it operates. They should also sufficiently understand the system operating principles so they are able to determine why components may fail. They should also be aware of what may be dangerous actions when servicing such an installation. Normally the potential risk to personnel will increase with the size of the system. Care with batteries should be well covered in any training course.

The following should therefore be included as part of a training programme:

- Explanation of how a solar module works, including the meteorological variability of solar irradiation.

- The purpose of blocking diodes and shading diodes.

- How a solar module is built, and how it should look when it is in a proper condition.

- If a charge regulator is used, the charge regulator should be explained and demonstrated.

- The battery’s electro-chemical principles, and how it should be properly maintained.

- Safety with batteries. Special training should be given on how to handle the electrolyte properly, including protective clothing and goggles, in order to prevent any accident.

- A special note should be developed covering how to deal with hydrogen [and other dangerous gases] and how it behaves and how it should be ventilated to avoid accidents.

- The service personnel should be trained in how to identify a fault in the system.

- The service personnel should be trained in taking measurements and performing regular maintenance on the system.

- A routine procedure should be developed so that the responsible person can obtain the necessary information when the service work is undertaken. [A record keeping and reporting system should be established.]

- Relevant occupational safety and health regulations should be included as part of the training programme.

# Wind power

Wind energy is an option where the wind is the preferable source of energy. There are two design methods of using wind energy specified below.

Rule of thumb formulae

Based on 4m/s average wind speed

Horizontal axis Watt Hour versus Swept Area

75-100 kWh per square metre per year. (ie 100 kWh/m2/y)

eg If the  swept area is 2 m2 gives 2*100 kWh = 200 kWh per turbin per year.

Vertical axis Watt Hour versus Swept Area

eg Small Scale Turbine

Less than 4m2 Total Swept Area

240 kWh per square metre per year. (ie 240 kWh/m2/y)

eg If the  swept area is 2 m2 gives 2*240 kWh = 480 kWh per turbine per year.

eg Large Scale Turbines

700 kWh per square metre per year. (ie 700kWh/m2/y)

eg If the  swept area is 4 m2 gives 2*700 kWh = 1400 kWh per turbin per year.

When selecting wind power – generators the following should be taken in to consideration:

- Vertical turbines seems to be more reliable.

- Turbine model should have references available from use in harsh weather conditions.

- Turbines should be environmental friendly (low noise, should not kill birds etc).

- Turbines should have long warranty time and long lifetime.

- Turbines should also produce power during heavy storm.

## Vertical axis generators

Advantages:

- Easy to install.

- Very reliable.

- Low maintenance.

- Long lifetime.

- Very low noise.

- Power available where low insolation prevents use of solar PV generation.

- Renewable energy source with associated cost savings.

Disadvantages:

- Rotating parts.

## Horizontal axis generators

Advantages:

- Easy to install.

- Power available where low insolation prevents use of solar PV generation.

- Renewable energy source with associated cost savings.

# Wave Activated Generator (WAG)

Wave activated generators are used on tail-tube buoys or combined with solar power.

Advantages:

- Relatively high energy density in floating AtoN with typically 60 - 100W output power.

- Renewable energy source with associated cost savings.

Disadvantages:

- Normally be used on tail-tube buoys, which maybe inconvenient to handle.

- High capital cost.

- High maintenance cost - typically installations are serviced at yearly intervals.

- Limited availability – single source.

- Flora and fauna might limit the use of some types of WAGs.

Comment:

- Technology still under development.

- Very high technical maintenance using currently available machines.

- Moving and rotating parts.

- Subject to damage under local weather conditions, e.g. freezing rain, typhoon.

- Very noisy.

- Kills the birds.

- Must be stopped during storm.

- No power production during storm.

- No power production under 3 m/s wind speed.

- Can be destroyed by vibrations in the structure.

Comment:

- The wind generator can be used as primary source of power generation but it should be considered to have some form of backup power source. Permission may be required for siting of the wind turbine.

# Fuel Cells

Fuel cell technology is quite new and is under continuous development. The fuel cell can be used as primary energy source or in combination with PV or wind generator (Hybrid System) on AtoN in remote areas.

Advantages:

- No moving parts in the Proton Exchange Membrane (PEM) cell.

- Low tech maintenance.

- No pollutant emissions.

- Low operational costs.

Disadvantages:

- Refuelling problems.

- Stack lifetime is limited.

- Low temperature performance for some types.

Comment:

- There are two types of fuel cells available on the market relevant to AtoN.

- PEM (hydrogen as fuel)

The PEM can be used on medium and major fixed lights in remote areas.

- Direct Methanol Fuel Cell

This technology still has to be proven in AtoN for small and medium lights, as well as buoys.

# Gen sets

## Diesel Generators

Generally used for high power requirements on fixed AtoN at remote places or as backup for mains electricity.

Advantages:

- Good cost to power ratio.

- Long established technology.

- Power is independent of most weather conditions.

Disadvantages:

- Complexity of installation.

- Dedicated space required, i.e. engine room needed.

- Expensive to maintain.

- Produces noise and atmospheric pollution.

- Regular refuelling required.

- Unattended service interval is short, typically 4 – 6 months.

- Fuel storage environmental risk has to be addressed at each site.

Comments:

- Renewable energy systems should be used in place of diesel generators wherever possible. Diesel generation may provide the reserve part of a hybrid system, or may be provided as an emergency power source.

- Installation of a diesel generator system may be considered necessary where domestic power is required.

## Petrol/Gas Engine Generators

Generally these power systems are used in a manner similar to the diesel generator systems described in section 4.4.

Advantages:

- Refer to Diesel Engine Generators.

Disadvantages:

- Refer to Diesel Engine Generators.

    - Fuel storage and transport safety implications.

    - Less durable than diesel engine generators.

    - Additional and more frequent service requirements.

Comment:

- For these reasons petrol engine generators are not recommended for fixed installations.

# Direct Gas (LPG)

Formerly gas lanterns were used, particularly on buoys, due to the high reliability of the systems.

Advantages:

- High reliability .

Disadvantages:

- Expensive to purchase and operate.

- Large storage space required for low power output.

- Hazardous nature of the fuel creates personnel safety and environmental risks.

Comment:

- This technology is being phased out in most countries.

# Future Possibilities

This section includes technologies that have not been fully tested to the reliability expected by IALA or technologies that are still under development and will be kept under review. The stated information about these technologies might not be up to date and readers are encouraged to consult the internet and other sources as required.

## Seawater Battery

Seawater serves as the electrolyte which when introduced starts the electro-chemeical process. This technology is typically used in applications which requires a power source to remain dormant for a long period before being required once immersed in seawater. Typical applications include life jackets etc. In its present condition the technology needs to be improved before this type of battery can be recommended for AtoN systems.

## Tidal Power

Tidal Generators can be classified into two types: Tidal Stream Systems harness the kinetic energy of the tidal stream by means of a turbine. Barrage systems harness the potential energy of tidal streams by virtue of the difference in head of high and low tides. There is currently much research work being focussed on the conversion of tidal energy into electrical power for transmission into the electrical grid. The envisaged generators are therefore on a much bigger scale than that required for AtoN’s.  There may be a future for this type of technology in AtoN applications once research work is translated into viable products for the market.

## Stirling Engine Generators

- Since the beginning of the 19th Century, the Stirling Cycle has been understood as being a viable way of producing a reciprocating engine using an external power source. It’s advantage is that any fuel can be used to power such an engine. However, there isn’t many commercial applications of this technology being used.

## Thermo Electric Generator

- These work by producing direct current across, for instance, p-n junctions set between hot and cold plates using the Seebeck Effect. In a practical sense, any fuel can be used to create the “hot” side and there have been commercial applications which require small amounts of DC current from a reliable source. Unmanned space satellites have used this for power using radioisotope decay as a heat source. Unfortunately, it’s very inefficient. Typical commercial applications are lower than 10 Watts

# Hybrid Power Source.

The advantages of Hybrid systems lies in the mix of sources chosen matched against the need to reliably supply an AtoN power system.

- If the power storage system has been designed to have an extended period of autonomy I.e. Battery heavy, then if the system should become depleted, full recovery could take a very long time to achieve.

- If the power storage system has been designed to have a shorter period of autonomy I.e. Battery light, then if the system should become depleted, full recovery could be achieved in a relatively short period.

However the design of the system autonomy is normally related to:

  - The ability to autonomously recover the charge.

  - The ability to attend the system to recover / repair.

Should the situation be as in 1 above then due consideration should be given to employing a hybrid power system.

Design considerations:

- Selection of Energy Storage solution

  - Energy storage must be sized to accept the peak current output from multiple sources concurrently.

- Selection of multiple input - hybrid solutions

  - Consideration to the mix of technologies. Ideally select devices of differing genre I.e. Passive and mechanical.

- Selection of a regulation system

  - Due consideration should be given to the mixing of regulators and the parallel connection of the outputs. I.e. Diode protection

|  | Fuel cell | Generator | Solar | Wind | Wave | Mains/Grid power | Primary cell |
| --- | --- | --- | --- | --- | --- | --- | --- |
| Fuel Cell |  | 0 | ++ | ++ | + | ++ | 0 |
| Generator | 0 |  | ++ | ++ | 0 | ++ | 0 |
| Solar | ++ | ++ |  | ++ | ++ | + | ++ |
| Wind | ++ | ++ | ++ |  | 0 | + | + |
| Wave | + | 0 | ++ | 0 |  | 0 | 0 |
| Mains/Grid power | ++ | ++ | + | + | 0 |  | + |
| Primary cell | 0 | 0 | ++ | + | 0 | + |  |

Key to table:

++ - Preferred

+ - Recommended

0 – Not Recommended