Development of Lithium Polymer Battery for AtoN in Korea

Battery R&D Center

EIG Ltd, Cheonan 330-814, Korea

Overview

The light buoy is a kind of safety facility for maritime navigation with a purpose of leading the vessels for navigating, docking and sail-off. An advanced rechargeable battery is required for stable power supply for navigation aid buoy as the high magnitude LED lamps, real time location/control for navigation aids and e-Navigation support systems with maritime climate observation equipments have recently been deployed.

The currently prevailing battery for navigation aid buoy is lead acid battery, of which the main materials are lead and fiber reinforced plastics.  The battery, mainly due to the lead contained, incurs environmental problems.  In addition, the energy density of the bulky lead acid battery is lower than the other type of batteries.  The lead acid battery is less efficient and short-lived in the tough maritime condition, thus making the management of the maritime transportation facilities even more difficult and costly.

The NiMH batteries have just been introduced to address the problems.  However, the low energy density-both volumetric and gravimetric- stemming from the low operating voltage of the chemistry restricts the reduction of the volume and weight of the batteries.  Besides, the alkaline electrolyte does not prevent the rapid degradation of the battery when used in the tough maritime conditions.

On the contrary, due to the higher energy density resulting from the higher operating voltage than the other batteries e.g. NiMH batteries, lithium rechargeable batteries offer an opportunity to reduce the weight and volume of the batteries.  In addition, the organic electrolyte of the lithium rechargeable batteries improves the discharging performance at low temperature.  As a result, the bulk of the small rechargeable battery market is shared by lithium rechargeable batteries and NiMH batteries, with the former surpassing the latter increasingly.  The eco-friendly batteries are gradually replacing the lead acid and NiCd batteries in the large format battery market as well.  The development of large and compact lithium rechargeable batteries contributed to enhancing the overall capacity of the batteries.  However, it also addresses the safety issue with increasing number of incidents of heating and fire.  The absolute safety is critical especially for the large format batteries as with larger capacity and higher voltage.  Consequently, the development of safer battery design technology and safer battery module and system design technology is actively pursued.  As per the active materials for cathode which is closely tied to the safety of the batteries, enormous amounts of research and development are conducted around the safer materials, including the surface treatment and improvement of the stable LiNi1/3Co1/3Mn1/3O2, the new composition of LiNiXCoYMNZO2 and the LiFePO4 chemistry known to be intrinsically safe. Therefore, this study is focused on the lithium battery, particularly lithium polymer battery which is believed to be safer than the other types of batteries.  The lithium polymer battery reviewed in this paper is designed with LiFePO4-based cathode, which has superior safety features to the oxide-based cathodes.  Besides, a 3.6kWh battery pack has been built with the afore-mentioned unit cells for the purpose of comparative research with the lead acid battery system.

Method of Experiment

For this study, 15Ah cells have been built based on LiFePO4 cathode and graphite anode with advanced lithium polymer battery design technology.  A unit module is composed of 20 15Ah cells connected in parallel.  The electrical properties of a battery pack of 12.8V 300Ah containing 4 modules connected in series have been reviewed in the study.  In addition, a 12.8V 300Ah battery has been connected to the navigation aid buoy system for a test under real application environment.

The battery packs were investigated cycle life and discharge characteristics with discharge current and temperature using cycler and performance connecting buoy light, controller and solar cells on land before test on the sea.

Outcome

Performance test for 12.8V 300Ah battery pack

Discharge characteristics with discharge current is shown in Table 1 and Fig.1 shows better electrical performance than the lead acid battery as no capacity fade is observed at the varying rate of discharge current.

Table 1 Capacity retention with discharge current

| C-rate | Results |  |
| --- | --- | --- |
|  | Capacity | Retention |
|  | Ah | % |
| 0.1C | 304.8 | 100.7 |
| 0.2C | 304.1 | 100.4 |
| 0.3C | 302.8 | 100.0 |
| 0.5C | 303.9 | 100.3 |

Fig.1 Discharge rate capability

Fig.2 shows discharge characteristics with discharge temperature. This showed that it has excellent discharging performance at low temperature and is able to operate below 0℃ because it sustained more than 80% of initial capacity at -10℃.

Fig.2 Discharge voltage profile with temperature

Cycle life is shown in Fig.3. The result proves the excellent life performance superior to the other types of lithium batteries with LiCoO2 or LiNiXCoYMnZO2 cathodes as well as the lead acid battery as more than 90% of the initial capacity has been retained after 800 cycles.

Fig.3 Cycle life

Performance test for 12.8V 300Ah battery pack connecting buoy light, controller and solar cells

The battery pack was connected with solar cell, buoy light, controller and data recorder as shown in Fig.4 and tested to monitor the variation of the current consumption and voltage profile when buoy light was turned on and off.

Controller

Buoy light

Controller

Buoy Light

Solar cell

Battery pack

12.8V300Ah

Data recorder

Fig.4 Experimental Apparatus

Buoy light was able to operate more than 569hrs(about 24 days) under the condition that buoy light was turning on all days as shown in Fig.5.  From the test result, the 12.8V 300Ah battery system is estimated to be able to run the buoy light for about 50days assuming 12 hours of daily operation.  The test was carried out until buoy light was completely turned off by itself at 5 to 10℃.

Fig.5 Operating time of buoy light without sunlight

Fig.6 shows a voltage profile and current consumption when buoy light was turned on. During the test a stable current consumption of 2.3A was observed while the buoy light is on, and the operating time was around 14 hours from the light turned on at 18:00 until it turned off at 08:00 in the following morning.  The voltage of the battery system, when measured after the light turned off, was about 13.3V at 90~90% of SOC(State of Charge).

Fig.6 Profile of voltage and current in operating buoy light

Fig.7 shows a voltage profile and current consumption when battery pack was charged by solar cells. Maximum charging current, voltage and SOC% were about 3A, 14.1V and 95%, respectively. The reason why charging current was small was low intensity of sunlight in winter season.

Fig.7 Profile of voltage and current in charging battery pack by solar cells

As a conclusion, the lithium polymer battery system designed with LiFePO4-based cathode and graphite-based anode sustained over 90% of retention capacity after 800cycles with negligible amount of capacity fade at different rate of discharging current and excellent discharging performance at low temperature below 0℃.  With the reduced weight-less than 70% of the existing lead acid battery, it will also enable the handy management of the battery system in maritime environment.

Future Tasks

The lithium polymer battery designed with LiFePO4-based cathode and graphite-based anode will be tested to verify performance on the sea and make up for the weak point through this test.