Trinity House Lighthouse Service Approach to Planned Preventative Maintenance of Lighthouses

# Background

Trinity House has operated a computer based planned maintenance system for the past 15 years or so on a variety of software packages, currently the system is being operated on a COSWIN software package and a replacement system is being sourced.

The majority of Trinity Houses lighthouses have been modernised in recent years, there are seven major lights to be completed by 2007. At the end of this program all stations will be fitted with modern control systems built to a standard either using dedicated electronics or PLC’s, using standardised components. As far as practical standard cubicle and system build is used in order to minimise training and spares holding.

All of the stations have remote monitoring and control via telemetry from Harwich, including critical analogue system monitoring.

Mainland stations are typically battery powered floating charge from the mains, backup alternators are provided at DGPS stations. Offshore stations are either solar powered or solar/diesel hybrid or solar/wind/diesel hybrid. In the case of hybrid stations the solar pack is the primary power source, the alternatives being back up or supplemental power supplies.

All stations have comprehensive documentation including operating instructions, as fitted drawings of all systems, maintenance instructions, parts lists and makers manuals. This documentation is produced to an established procedure and a high standard. Prior to hand back of a re-engineering lighthouse from Engineering to Operations all appropriate training is completed.

The latest round of modernisation has resulted in much improved reliability, the design critically designs out previously unreliable equipment. On completion of each modernisation project a formal hand over procedure between Engineering and Operations ensures that the high standards are maintained.

# The alternative approach to RCM being taken by Trinity House

Trinity House takes the view that the RCM approach is more appropriate to maintenance systems, which are inherently more complex, and with lower levels of reliability being experienced within their lighthouse population. A less rigorous approach has been taken in reviewing the maintenance need whilst retaining a structured review process. Using the approach taken Trinity House is able to quickly adapt it’s maintenance methodology to the changing technological demand.

Working from the basis that all stations have been engineered to a high level of reliability and that the current maintenance programs are maintaining the stations in a condition which enable Trinity House to exceed all IALA reliability and availability requirements a review of the maintenance need was carried out. All stations double or triple redundancy built in to the most critical processes, which makes them very resilient as demonstrated by the low level of casualties experienced.

As part of a five-year rolling program of maintenance performance the “Maintenance Way Ahead 2002-2007” report was produced, this builds on the previous report covering the period 1995 – 2000.

The 2002-7 report identified that some changes were desirable in the way that maintenance was carried out on Trinity House Lighthouses to reflect the substantial improvements in reliability and maintainability, which was resulting from the latest lighthouse modernisation program.

The existing maintenance program was based on contract attendants visiting each land or island station monthly (tower station attendants are usually Trinity House operators) to carry out husbandry duties. Twice yearly a team of two or three technicians visit each station to carry out intrusive planned maintenance. This workload resulted in an average of 30 technician days for each station, which when taken with the management, support and planning overhead results in an average annual charge of £20k per station.

It was recognised that this level of maintenance on modernised stations was unnecessary and that intrusive maintenance on electronic systems was not capable of enhancing their reliability. It was decided that the maintenance could better be carried out in a three tiered system: -

Level One – a none intrusive service primarily confirming the station functionality and key system checks, carried out during the monthly station visit by the attendant.

Level Two – an annual full station service carried out by a team of technicians, carrying out both Planned Preventative and Planned Maintenance tasks.

Level Three – An irregular maintenance routine to deal with major overhauls or repair work, for instance the overhaul of diesel engines (running hours driven), the mercury bath cleaning (five yearly), battery changes (condition driven) or glazing repairs (condition driven). Typically this work will be planned a year in advance and form part of the Planned Preventative Maintenance for the station. Specialist technician teams typically will carry out this work, possibly as a separate visit to the routine PPM visit.

It is considered that the above maintenance strategy will reduce the maintenance technician effort by about 35%, resulting in both depot and manpower reviews.

At the same time it was recognised that certain systems had less than optimal reliability, in particular Fog Signal systems, these issues are addressed via an established internal Defect Acquaint system with Operations requesting Engineering to review the system designs.

In order to determine the maintenance requirement of the modernised stations the following approach was taken:-

The existing library of Standard Maintenance Routines was reviewed and updated to reflect the changing equipment levels on the stations. As an example as there are no longer any working pneumatic fog signals no references to these are carried over into the updated lists.

A review of spares holding was carried out against the standard station fit out and found to be well managed.

For each station:-

- Check that the station exceeds IALA availability requirements

- Desktop review of Planned Preventative Maintenance and Planned Maintenance of the station and the man-hours involved over the past two years.

- Review that all documentation is up to date

- Review the casualty history of each station with particular regard to whether the level of maintenance had an impact on the cause of the casualty.

- Identifying the major station systems: -

  - General

  - Batteries

  - Engines

  - Health and Safety

  - Aid to Navigation

  - Telemetry

  - Premises

- Review current Planned Maintenance routines for station

- Station visit by a Mechanical/Electrical and Control/Communications line manager and two technicians to review each systems maintenance requirements in light of:-

  - Station equipment fit out

  - Station design

  - Current Maintenance routines

  - Station reliability.

- Select from the revised library of standard maintenance routines the appropriate ones for the station being reviewed.

- Produce the revised maintenance routine for the station together with agreed planned hours.

An example station is St Bees, located on the North West coast, this was reviewed according to the above methodology and revised maintenance routines determined based on monthly attendants visits and an annual technician visit. The outcome is a reduction in planned time on station by about 15% annually. This review was carried out in one day, with a further office halfday for the two line managers.

Attached are station characteristics and the revised maintenance routines, for both the attendant and technician.

Trinity House Lighthouse Maintenance Review Way Ahead

The revised routines are being piloted on fifteen stations during 2002-3 and further fifteen or twenty stations will be added during 2003-4. All the pilot stations in 2002-3 are mainland stations, battery powered, main’s float charge. Several of the stations in 2003-4 will be solar powered island stations and one will be a diesel cycle charge station.

By 2004-5 all modernised stations will be operating to the revised maintenance schedules

In view of the forthcoming replacement Maintenance Planning System software it has been decided to run the pilot system in paper format until the new software is introduced during 2003-4.

This program has an impact on depots, manpower requirements both technician and supervisory, manpower deployment and support in areas of helicopter and ship usage.