Comment – IALA Guideline 1008

The following comments regarding IALA Guideline 1008 have been provided by James Collocott, Lighthouse Services, Transnet National Ports Authority, South Africa.

Firstly, well done on excellent Guidelines that were submitted to the last Council meeting!

I have two minor items which I would like to bring to your attention, which you may want to consider for inclusion in the above mentioned guideline.  I do accept that this may have been considered during the drafting period.

- Top of page 14, under the heading

Table 5              DGPS signals

Should consideration not be given to include a parameter on the transmitter itself, e.g. Transmitter On / Fail?

- Top of page 15, under clause 5.4.1

Have you considered to include "Bus bar failure"?  We have found this to be very useful, as mains supply could be available in the control panel, the mains contactor is activated, but due to a faulty condition (e.g. mains contactor contacts failure, or tripped circuit breaker), there is no power on the bus bar of the control panel and the engine does not start as this is undetected.  The same applies for the output of the diesel generator.