| TECHNICAL PROCEDURE TP021 |  | # Sonnennschein GF Y 12 063 Battery Maintenance and Conditioning |  |
| --- | --- | --- | --- |
| 1 | 18 April 2008 | A. Williams | R. M. Tomkins |
| Issue | Date | Written By | Approved By |

# Introduction

The batteries are “maintenance-free” whilst in service, in that no topping-up of the electrolyte is required.  Maintenance effort is, however, required to ensure proper storage, use and replacement at the end of the design life.

Service labels as shown on drawing SBD/130 should be used to provide a maintenance record for each battery.

Observe the safety instructions given on the service label, in the Modular Superstructure Reference Manual and in the Trinity House Health and Safety Instructions.

# Supply

All gel batteries (see Specification S041) should be supplied from the manufacturers fully charged and capacity tested immediately prior to delivery, test certificates being included.  If this is not feasible the batteries should be acceptance tested at the TH Depots in accordance with Section 6 before service.

# Storage

The same care should be taken of batteries whether stored ashore or afloat.

Refresher charge the batteries every 6 months, returning the batteries to the Depots if necessary.

Batteries should not normally be held in store for more than 1 year, the oldest batteries being used first.

If a battery is found to have been in store for more than 1 year, capacity test as described in Section 7, to check it still has the full rated capacity prior to introducing to service.  Return batteries to the Depots for this to be undertaken if necessary.

Check that the off-load voltage of all batteries is greater than 12.6V before introducing to service.

# Service

The batteries have a service life of 8 to 10 years.  The only maintenance normally required whilst in service is checking the security of the battery fixings and terminals, and smearing the terminals with petroleum jelly to protect the contact surfaces.

If a casualty occurs due to a solar system failure, which cannot be attributed to a lantern failure, replace all the batteries as a precaution.  Return the batteries to the Depots for capacity testing as described in Section 6.

Where a battery has been in service for less than 2 years, and a capacity test shows it still has the full rated capacity, this may be used for another 4 years service.  Otherwise the battery should be disposed of in acordance with TH procedures.

# Battery Charging

Whenever the batteries are to be charged this should be undertaken using a constant voltage battery charger set to a charge voltage of 14.4V.  The current should be limited to 15A per battery.

Continue the charge until the current remains constant over a 3 hour period, or allow 12 hours for the charge if the current cannot be monitored.  Recharge the batteries for 24 hours following a capacity test discharge.

Refer to the “Battery conditioner unit settings” specification when using these units to charge the batteries.

# Capacity Test Procedure

The CCD SPA 8250 battery conditioner units may be used, conditioning one battery with each CCD unit.

6.1	Charge the battery as described in Section 5 and undertake the discharge test between 1 and 24 hours after completing the charge.

6.2	Discharge the battery using a constant current load at the 5 hour rate until the voltage falls to 10.5V.

The 5 hour rate current is given by:

I5 = C55 = 635 = 12.6 A

Where C5 is the 5 hour rate capacity of the battery.

The CCD SPA 8250 battery conditioner units discharge the battery at a constant current of 12A (nearest discharge current setting).

6.3	Measure and record the temperature by placing the sensor against the side of the battery.

6.4	Measure and record the battery voltage at 30 minutes intervals.

6.5	A battery with a voltage below 10.5V after 4 hours discharge has failed the test.

6.6	Stop the discharge when the battery voltage falls to 10.5V.  Record the duration of test and actual voltage.

6.7	The capacity of the battery is given by:

##### Ct = Ih

Where	t	is the battery temperature

I	is the discharge current

h	is the duration of the discharge down to 10.5V

The capacity of the battery at the reference temperature of 20ºC when the battery temperature is less than 20ºC is given by:

##### CT = Ct1−0.007(20−t)

When the battery temperature is greater than 20oC the capacity at 20oC is given by:

##### CT = Ct1+0.005(t−20)

The full rated capacity of the battery at the 5 hour discharge rate and reference temperature of 20oC is 63Ah.

6.8	Batteries achieving these values should be recharged as described in Section 6 and are then acceptable for service.  This is done automatically by the CCD SPA 8250 units.

# Cycle Conditioning

7.1	Batteries not achieving the full rated capacities above may be cycle charged and discharged up to 6 times.  Three cycles are completed automatically by the CCD SPA 8250 unit in each operation (see Appendix A for appropriate settings).

7.2	If the battery fails to achieve 50Ah capacity after 3 initial cycles the battery should be rejected and disposed of by the appropriate route.

7.3	If the battery achieves 50Ah capacity but fails to achieve 63Ah, 3 further conditioning cycles may be undertaken to see if the 63Ah capacity can be achieved.

7.4	Batteries achieving 63Ah capacity should be recharged as described in Section 6 and are then acceptable for service.  This is done automatically by the CCD SPA 8250 units.

NOTE		The CCD SPA 8250 unit should only be used to cycle one battery at a time.  Parallel connection of batteries will result in insufficient charge or discharge currents as the batteries are cycled.

APPENDIX A

| Battery Conditioning Parameters for a Sonnenschein Battery Type GF12 063Y | Parameters |
| --- | --- |
| ## Number of Conditioning Cycles A ‘Conditioning Cycle’ consists of an Ah Capacity Monitored Discharge followed by a Recharge. The more cycles performed, the nearer the battery will get to its maximum capacity. However, more Cycles take more time. An optimum Time/Capacity performance can usually be achieved with 2 or 3 Cycles. | 5 |
| ## Discharge Current The nominal Current at which the battery is discharged. This can be adjusted to suit the battery type and/or match the conditions under which the battery will be used in service and so give a realistic indication of the capacity available when the battery is used in a particular situation, as the capacity a battery will deliver in service will depend on the current at which it is discharged. This current is set at approximately 12V and will change as the battery voltage falls during discharge. As the current is continually measured and the Ah capacity calculated from the time integral of discharge current, it is not necessary to maintain a constant current to obtain an accurate capacity value. As with the number of cycles, discharge current will affect the time taken to condition a battery. It is normal, for capacity testing, to discharge a battery at a rate of C/3 to C/4. | C5 Capacity = 12.6A 5 |
| ## Discharge Terminate Voltage This is the voltage at which the SPA-8250 determines the battery to be fully discharged and terminates the discharge cycle. This should be set to represent a minimum working voltage below which the battery should not be discharged to prevent damage. | # 1.75vpc = 10.5V |
| ## Post Discharge Rest Time This allows the battery to be rested following a discharge, before the Bulk Charge cycle is started. Battery manufacturers may recommend a rest period between full discharge and re-charge. | # 0 |
| ## Bulk Charge Current This is the upper limit for the charge current when in Bulk Charge Mode. This should be set as per recommendations from the battery manufacturer to prevent damage to the battery by over current or transient over heating during the bulk charge phase. | # C10 Rate = 6.3A Maximum charge rate = 15.7A ### Charge current = 12A |
| ## Bulk Charge Terminate Voltage This is the battery terminal voltage at which the Bulk Charge Phase will be terminated and the charger switched to float charge mode. This voltage should be set according to the battery manufacturers recommendation. | 2.4 vpc = 14.4V @ 20 °C |
| ## Maximum Battery Temperature This is the maximum temperature (in degrees centigrade), as measured by the battery temperature sensor, which the battery may rise to, before the charger is turned off to prevent battery damage due to over heating. The battery will have a significant thermal capacity and so with the sensor fixed to the outside of the battery (usually fixed to the – ve terminal clamp), there will be difference between the measured temperature and the batteries internal temperature. If maximum battery temperature is considered to be critical, allowance should be made for this difference in setting the maximum battery temperature. | 45 °C |
| ## Charge Foldback Temperature This is the temperature, below the Maximum Battery Temperature, at which the charge starts to lower the charge current to keep the battery temperature within limits, whilst still maintaining charge. For example, if the Maximum Battery Temperature is set to 60C and the Foldback set to 5C, if the battery temperature reaches 55C, the charger will start to reduce the current in an effort to find a current at which the charge can be maintained and the temperature maintained below the maximum limit. If the temperature continues to rise, the current will be proportionally lowered to zero when the temperature reaches the maximum set. | 5 °C |

| ## Float Charge Voltage This is the voltage at which the ‘Float Charge’ will be maintained. The voltage is set for a battery temperature of 25C. This should be set according to the battery manufacturers recommendations for float charging the battery. | 2.35vpc = 14.1V @ 20 °C |
| --- | --- |
| ## Float Charge Voltage Temperature Compensation This is the temperature compensation for the float charge voltage for battery temperatures above 25C. It represents a reduction in voltage as the temperature of the battery increases and is set as a number of millivolts per cell per degree centigrade. This should be set according to the battery manufactures recommendations for float charging the battery | -5mV/C/ °C |
| ## Float Charge Time This is the length of time (in hours) that the float charge will be maintained for. After this time, the charge will be terminated and the next discharge cycle (if any) commenced. | 8 Hour |
| ## Final Float Charge Time This is the length of time (in hours) that the float charge will be maintained for, for the final float charge (Last or Only Cycle). After this time, the charge will be terminated. | 24 Hours |
| ## Post Charge Rest Time This allows the battery to be rested following a charge, before the next discharge cycle is started. Resting the battery following a charge will allow the battery temperature to return towards ambient and may affect the capacity achieved and any effects due to temperature rise during discharge. | 1 Hour |
| ## Charge Before Discharge When set, this forces the SPA-8250 to perform a charge cycle at the beginning of the conditioning regime, so that the first discharge cycle always starts with a fully charged battery. | NO |