Association Internationale de Signalisation Maritime

International Association of Marine Aids to Navigation

and Lighthouse Authorities (IALA – AISM)

James Collocott

IALA Council Member 							16th October 2009

South Africa

Dear James,

Response to comments on IALA Guideline 1008 on Remote Monitoring & Control of Aids to Navigation

Many thanks for your perceptive observations to EEP on IALA Guideline 1008 on Remote Monitoring & Control of Aids to Navigation.

Transmitter On/Fail was not included as a monitored parameter in Section 5.3.4 for  DGPS as the Signal to Noise Ratio and Signal Strength are both monitored.  It is felt that Transmitter On/Fail is effectively monitored through these parameters.  Additional transmitter On/Fail signals would also add a further signal loading to the RCMS.

Monitoring bus bar failure directly is an interesting concept.  In the example you quote, the failure of a mains fail generator set to detect a mains failure arises from the method used to detect mains failure in the generator control system.  Most generator control systems have in-built mains supply detection which is effectively connected to the bus bar and therefore would not benefit from additional monitoring.

In a remote control and monitoring system, mains failure arising from either utility mains supply or diesel generator set failure at the bus bar would be detected through the signals monitored in Section 5.4.1 (for detecting mains failure) or through loads such as battery chargers in 5.4.2.  It was felt this provided adequate monitoring of the mains power supply.

Thank you again James for your positive contribution to the Guideline.  We hope you find the above philosophy acceptable and the Guideline useful.  Also many thanks for your continuous support to your old Committee.  I am looking forward to meet you again in Cape Town.

With kind regards

Ómar Frits Eriksson

Chairman, IALA EEP Committee