4.2	Lifetime

For conventional technologies, the “rated average lamp life” is the point at which half the lamps cease to emit light. All sources lose light output over time, but generally not more that 15–20 percent over the rated lamp life as defined by complete, lights‐out failure. A well‐designed LED package, however, would typically have a very long‐rated life, as conventionally defined, but, because it is so long, would also have more lumen depreciation over that life than conventional

technologies. Accordingly, we need a new approach. Whatever the stated lifetime of any lighting product, it is a statistical measure of the performance of a given design. For an individual LED package, lifetime has typically been considered to be the hours of operation at which the light output has fallen to 70 percent of its original value (“L70”).

The lifetime claims for LED luminaries are very long and around 50,000hours. This is somewhat longer than 10 years.  But to specify an LED array for 50.000 hours, means that every system component must be rated for 50.000 hours. For a manufactory it is not easy to address the reliability of all components. The LED system reliability is based on several components: See figure 1

RSYSTEM= RELECTRICAL* RCONNECTIONS* RLEDS* ROPTICAL* RTHERMAL* RMECHANIC

Figure 1.

Lumen maintenance

The concept of ‘lumen maintenance’ is well understood in the LED lighting industry: the light output from power LEDs is highest when new, and declines gradually over time. All reputable power LED manufacturers conduct long-term performance testing of each variant of their products, and publish lumen maintenance

But lumen maintenance is not the only failure mode of power LEDs: they can also fail catastrophically, just like a conventional light bulb, and just like every other electronic or semiconductor product. In the case of a LED product the rate of this so-called ‘catastrophic failure’ is low, so low that the myth that LEDs never fail is still widely believed. Nonetheless, should a catastrophic failure occur, it could be of material significance depending on system design and the nature of the application.

In fact, there are a number of reasons why luminaire manufacturers should take account of catastrophic LED failure rates when designing a fixture. Perhaps the most obvious is that a catastrophic LED failure might leave a dark spot in an array.

This could lead the user to the conclusion that the fixture is malfunctioning, even if a photometric examination showed that light output is still at or above its specified level. Second, the concept of lumen maintenance has already been rehearsed above; any catastrophic failure, which eliminates the light output of an LED, will add to the decline over time in a lighting system’s output.

Third, and less obviously, a catastrophic failure in an individual LED can cause instant failure in a complete luminaire or section of a luminaire. In part, this depends on whether an LED fails electrically ‘open’ or fails electrically ‘short’. If it fails open, the power supply is cut off from every LED in the failed LED’s string (in other words, to every other LED connected in series with the failed device), and the whole string goes dark. When a LED fails ‘short’, on the other hand, current continues to flow through the string allowing the luminaire to continue functioning.

The foundation of reliability data

The long-term performance of LEDs, then, is affected by the rate of lumen maintenance and by the incidence of catastrophic failures; in combination, these two effects lead to a reduction in light output over time across a population of LEDs.

So the industry’s critical need is for a trusted process that allows for more accurate predictions of system performance and for higher confidence in the engineering and business decisions associated with a luminaire.

But the user’s confidence in such a model, and in the data that lie behind it, is a factor of the thoroughness of product testing carried out by the LED manufacturer. Therefore we start with a description of:

> Reliability models are derived from its tests

> What the raw test results tell users about LED behavior

> How lighting system designers can use this knowledge

How reliability models are derived

There is an infinite number of such conditions, so LED manufacturers cannot test for all possible conditions.

All LED reliability models are therefore the result of extrapolation from a base set of data. The extrapolation occurs in two dimensions: operating conditions (drive current, and board/junction temperature); and time.

Figuur 2. Cells needed for LM80-08 specification

What we see is the degree that temperature, current, and time affect lumen maintenance. We know for some Cool White LEDs that drive current has a strong relationship to lumen maintenance and ambient temperature has a very low correlation to lumen maintenance. These relationships vary from product family to product family and from manufacturer to manufacturer. Some manufacturers report a strong correlation between ambient temperature and lumen maintenance which should be clearly seen in their data.

The lumen maintenance of an LED must also extrapolate into the future. Again, LM-80-08 specifies a minimum of 6,000 hours of testing. The ENERGY STAR® Manufacturer’s Guide (September 2009) requires a minimum of 25 samples.

The industry-standard LM-80-08 lumen maintenance reports in use today do not provide all of the necessary information that luminaire manufacturers need in order to predict the lumen maintenance behavior of a population of LEDs.

As stated in the introduction, it is common-but inappropriate-practice for luminaire manufacturers to use LM-80-08 lumen maintenance ratings to define the operating lifetime of a complete luminaire.

But an extrapolation of the rating only produces the average (median) lumen maintenance of a single LED under stated operating conditions—in figure 3, the red curve shows median performance for a LED at 85°C, 0.35A. This median performance of a single LED ignores a spread of results from best to worst across a population of LEDs. A lumen maintenance rating based on the median result for a single LED overstates the lumen maintenance performance of 50% of LEDs, and understates the performance of the rest.

Lumen Maintenance Projection for White >3500 K

850C, 0.35A (T-junction  98oC ) Normalize to 1 at 24 hours

Figure 3. Long-term lumen maintenance data and L70 extrapolation

The industry-standard LM-80-08 lumen maintenance reports in use today therefore do not provide all of the necessary information that luminaire manufacturers need in order to predict the lumen maintenance behavior of a population of LEDs.

While LM-80-08 does not require information about the spread in lumen maintenance behavior across a population of LEDs, it is possible to derive information from the tests described above. And this information can be expressed as a probability that a single LED’s lumen maintenance will cross a given threshold after a given operating time at a given set of operating conditions. An example of such a probability curve is shown in Figure 4.

Catastrophic Failure Model

LED reliability, though, is not just a question of lumen maintenance. And while industry practice, as exemplified by the LM-80-08 standard, has focused on the production of lumen maintenance ratings for power LEDs, no such standard procedure exists for testing for catastrophic failure.

Philips Lumileds has therefore created a testing procedure that can be employed by any LED manufacturer. This uses the cells in the lumen maintenance testing regime (see Figure 4 above), and adds more highly stressed conditions. (see Figure 5).

Cool-White  stressed at

Tjunction _ xx°C, yyA

Estimated L70 failure rates, one sided 90% LCL

Figure 4. Lumen lumen maintenance distribution from lumen maintenance model

Figure 5.Cells used in catastrophic failure model example

This test set includes cells operating beyond the ‘recommended’ level and beyond the ‘maximum’ level. The data from these highly stressed conditions help to provide a greater degree of confidence in the extrapolations of the LEDs’ performance at normal operating levels. Note that cells “Y” are higher operating conditions than the recommended operating conditions. Note that cells “X” are higher operating conditions than the maximum ratings.

As with the lumen maintenance model, the observed catastrophic failures in the test cells are fed into a standard reliability software package in order to develop a catastrophic failure rate model for a single LED with temperature and drive-current acceleration factors.

Cool-white LED using TFFC

Estimated L70 failure rates, one sided 90% LCL

Figure 6. Impact of varying forward current in lumen maintenance model.

What the models tell manufacturers about LED behavior over time

Figure 6 shows examples of the lumen maintenance behavior of cool-white LUXEON Rebel LEDs, as predicted by the lumen maintenance model, when subject to different drive currents. Figure 10 shows examples of the lumen maintenance behavior of the LEDs when subject to different temperatures.

Cool-white LED using TFFC

Estimated L70 failure rates, one sided 90% LCL

Figure 7. Impact of varying junction temperature in lumen maintenance model.

Predicting the probability of failure of an LED array

So far, we have shown that lumen maintenance and catastrophic failures are two different kinds of LED behavior: they have different effects on a luminaire’s visual appearance and on its performance; and the operating conditions in a luminaire affect the behaviors differently.

This means that luminaire designers need to be able to refer to discrete predictions for lumen maintenance and for catastrophic failure rates.

But as observed above, the rate of lumen maintenance and catastrophic failures combine to produce a decline in system light output over time. So as well as being expressed as discrete values, lumen maintenance and catastrophic failure rates also need to be expressed in combination.

It is possible to combine the two values to produce a probability of a single LED failing either through passing a lumen maintenance threshold, or through catastrophic failure. Such a probability curve is shown in Figure 8.

Cool-white LED stressed at

T-junction  xx0C , yyA

Estimated combined failure rates, one sided 90% LCL

Hours

Figure 8. Combined lumen maintenance and catastrophic failure model.

A LED based luminaire or solution is a complex system comprised of many components each with their own behavior and expected performance over time. Because of the familiar lighting paradigm, light sources are usually considered to be the weakest link in the system and therefore garner the most attention. This is, in no small part, why standards activity has focused primarily on LEDs to date and because of this, LED manufacturers have a significant amount of data regarding the lumen maintenance and failure rates and modes of failure. It should be clear, however that in the new lighting paradigm, the light source, LED, is probably not the weakest link but in fact just one of a number of components whose lifetime must be understood. We hope that through our evaluation and explanation of both lumen maintenance and failure rates, the reader’s understanding of LED lifetime is better understood along with the following concepts; Lumen maintenance is not a proxy for LED lifetime, the lifetime of an LED system is based on achieving minimum levels of light output, and lastly, by designing for reliability, luminaire manufacturers can maximized design, minimize costs and appropriately warranty their systems.

The purpose of this paragraph was to draw attention to the many aspects of LED reliability and not to convey specific data. Any charts in this chapter are for a specific LED technology only and can change at any point in time.

(bibliography Evaluating the Lifetime Behaviour of LED systems     Philips Lumileds)

4.3	Maintenance

There are several possible maintenance issues which may not be identified yet as the likely failure modes of an LED luminaire over the long term are not known. .  If an LED luminaire has a failure in one panel of its array, then it may be possible to replace this.  If this replacement happens after several years, the new panel may have a noticeably higher luminance which could effect the uniformity of the luminance distribution.

The pace of LED luminaire development is rapid.  This is very encouraging in that early shortcomings are being designed out at a fast rate.  However, if the LED luminaires in an installation last the whole of their service life (10 years), the original model may not be available.  This would mean the complete replacement of the luminaire after only about half the currently expected lifetime of an installation.  This possibility must be taken into when making cost comparisons between discharge and LED based luminaires.

The design of installations uses a maintenance factor such that the initial values of the LTPs are higher than that specified so the installation still complies at the end of the maintenance cycle.  The maintenance factor usually varies around 0.7-0.8.  The manufacturers of LED luminaires claim that the service life of the luminaire is reached when the output falls to 0.7 of its initial value, that is the maintenance cycle would be 10 years.  This may not be palatable to the road authorities who would prefer are more frequent monitoring of the installation with regard to spot failures and soiling etc.  Perhaps an enlarged definition of maintenance factor is needed to include LED luminaires.