## Risk Analysis
Date: 12-11-07
Risk analyse (lightning strike protection) |  |  |  |  | Vila R.S.António Lighthouse
INPUT DATA |  |  | Struture characterization
Local Keraunic index | 9 |  | C1 ; Coefficient
Coefficient C1 | 0.75 |  | Structure located in an area where there are other |  |  |  |  | 0.5
Coefficient C2 | 1 |  | structures or trees of the same height or higher
Coefficient C3 | 2 |  | Structure surrounded by lower structures |  |  |  |  | 0.75
Coefficient C4 | 3 |  | Isolated Structure |  |  |  |  | 1
Coefficient C5 | 5 |  | Isolated structure situated on a hill or promontory |  |  |  |  | 2
Height of tower | 46
C2 ; Strutural coefficient
Result of calculations |  |  | Roff | Metalic | Common | Flammable
Ng density of impacts per Km2, year | 0.78454
Nd expected frequency of impacts | 0.038725 |  | Metal | 0.5 | 1 | 2
on the structure |  |  | Commom | 1 | 1 | 2.5
Nc acceptable frequency of impacts | 0.00018333 |  | Flammable | 2 | 2.5 | 3
on the structure
E efficiency of protection to install ≥ | 0.99527 |  | C3 ; Stuture content
|  |  | Without value or not flamable | [5 empty] | 0.5
|  |  | Commom value or normaly flammable | [5 empty] | 2
If Na - Nc is negative it is not necessary | 0.038542 |  | High value or particularly flammable | [5 empty] | 5
protection |  |  | Exceptional value, irreplaceable or highly flammable, explosive | [5 empty] | 10
C4 ; Occupancy of the structure
|  |  | Unoccupied |  |  |  | 0.5
|  |  | Normally occupied |  |  |  | 3
|  |  | Difficult to evacuate or risk of panic |  |  |  | 7
C5 ; Consequences of impact
|  |  | No need for continuity of service and some |  |  |  |  | 1
effect on the neighbourhood
|  |  | Need for continuity of service and some |  |  |  |  | 5
effect on the neighbourhood
|  |  | Effect on the neighbourhood |  |  |  |  | 10
Table B.10
|  | E |  | Level of protection |  | I(kA) |  | D(m)
|  | Efficiency calculated |  | corresponding |  | Rated crest |  | Distance from start
maximum
Efficiency of protection to install ≥ | 1 | E > 0,999 |  | Nível I++ |  | (a) |  | (a)
|  | 0,99 < E ≤ 0,999 |  | Nível I+ |  | (b) |  | (b)
|  | 0,98 < E ≤ 0,999 |  | Nível I |  | 3 |  | 20
|  | 0,95 < E ≤ 0,98 |  | Nível II |  | 5 |  | 30
|  | 0,90 < E ≤ 0,95 |  | Nível III |  | 10 |  | 45
|  | 0,90 < E ≤ 0,80 |  | Nível IV |  | 16 |  | 60
|  | E < 0 |  | It is not necessary protection
Selecting the level of protection
if Nd ≤ Nc protection is not neccessary
If Nd > Nc you must install protection system of efficiency (E) and corresponding level of protection in selected table B.10
Additional measures: | (a) Struture protected by PDI with decrease protection radius
(b) Struture protected by PDI
Outcome of risk analysis:

## Wenner - Ground Resistivity
Local: | Vila Real de Santo António Lighthouse |  | Date: | 2007-11-12
Analysis of ground resistivity using the Wenner method
| Test electrodes depth | 0.3 | Meters
Depth | Distance between electrodes | Measured value (Ω) | groud resistivity (Ω.m)
Estimated |  |  | Simplified formula | Complete Formula
0.75 | 1 | 355 | 2230.536 | 2538.7973
1.5 | 2 | 104 | 1306.9056 | 1356.6145
2.25 | 3 | 57 | 1074.4272 | 1092.9393
3 | 4 | 35 | 879.648 | 888.2312
3.75 | 5 | 22.2 | 697.4352 | 701.8043
4.5 | 6 | 18.9 | 712.5149 | 715.6199
5.25 | 7 | 12.6 | 554.1782 | 555.9544
6 | 8 | 8.8 | 442.3373 | 443.4234
6.75 | 9 | 6.6 | 373.2221 | 373.9465
Profiles of resistivity
Ascendant: | Clay surface area and wet the bottom and rocky
Descending: | Surface area very dry and sandy area below
Plan: | Rocky ground, dry
Obs:
This is an area of dune area where the surface is dry and loose sand