|  |
| --- |
| IALA Guideline |

1039

Designing Solar Power Systems for Aids to Navigation

(Solar Sizing Tool)

Edition 2.0

June 2017

Revisions to this IALA Document are to be noted in the table prior to the issue of a revised document.

|  |  |  |
| --- | --- | --- |
| Date | Page / Section Revised | Requirement for Revision |
| June 2017 | Whole document  Section 1 | Revision according to the update of the Excel-sheet (tool) at IALA Workshop 2017 in Koblenz  General information on solar technology and batteries added |
|  |  |  |
|  |  |  |
|  |  |  |
|  |  |  |
|  |  |  |
|  |  |  |

1 INTRODUCTION 5

1.1 General Information on Solar technology 5

1.1.1 Types of solar cells 5

1.1.2 Lifespan 6

1.1.3 Current - Voltage Curve 7

1.1.4 Temperature Influence 7

1.1.5 Thermal Characteristics 8

1.1.6 Solar Panel Orientation 8

1.2 General Information on Batteries 9

1.2.1 Minimum and Maximum Capacity 9

1.2.2 Autonomy time 10

2 INPUT DATA 10

2.1 Solar Irradiation and duration of night 10

2.2 Latitude and Longitude 11

2.3 Orientation 11

2.4 Voltage 11

2.5 Electrical Loads 11

2.6 Switch Level 11

2.7 Solar Panels 11

2.8 Batteries 12

3 OUTPUT DATA AND ITERATION 12

4 END USER LICENSE AGREEMENT (EULA) FOR IALA SOFTWARE – IALA SOLAR SIZING PROGRAM 13

4.1 Software product licence 13

4.2 Miscellaneous 13

4.3 Limited Warranty 14

5 ACRONYMS 14

ANNEX A SAMPLE PAGE FROM THE SOLAR SIZING PROGRAM 15

# INTRODUCTION

This program provides an iterative method of designing a solar power system for fixed or floating AtoN installations. To keep the Excel workbook as simple as possible it has some certain limitations and factors that it does not take into account. These include:

* specific technical data for the products,
* temperature for any location or
* temperatures for batteries or panels
* land and sea reflection coefficients,
* rate of battery self discharge,
* seasonal or occasional loads.

To obtain the MS Excel workbook, including the password, please contact the IALA Secretariat via e-mail ([contact@iala-aism.org](mailto:contact@iala-aism.org)). Alternatively the MS Excel workbook is available for download at the IALA website. In addition there is a step by step manual provided which includes information on how to obtain meterological data.

Section 1.1 and 1.2 deal with some technical information on both solar panels and batteries, to assist with use of the solar sizing tool.

Sections 2, 3 and 4 provide specification information related to the use of the solar sizing tool.

A sample page from the Solar Sizing program is at ANNEX A.

## General Information on Solar technology

### Types of solar cells

There are basically three types of solar cells for photovoltaic (PV) systems, depending on the manufacturing process:

* Monocrystalline
* Polycrystalline
* Thin Film or amorphous silicon.

The materials used for the manufacture of solar cells are mainly:

* various types of silicon,
* gallium arsenide,
* indium copper diselenide and
* cadmium telluride.

Their selection of material depends on the panel’s intended application.

**The monocrystalline cell:**

It is made from the mineral "silicon", which is found in abundance in sand. A single "grown" crystal is gradually formed into a block. The cells are then cut into thin slices from 250 to 350 μm. The efficiency limit of the crystalline cell is around 35%. Currently this type of cell achieves efficiencies of 21%.

**The polycrystalline cell:**

It is made from molten silicon glass that is formed in a mould. It is cheaper than the monocrystalline cell, but its limit efficiency is 32%. Currently this type of cell achieves efficiencies of 19%. It is recognized because its colour is irregular and clearer than the monocrystalline and has a rectangular shape without cuts at the edges.

Polycrystalline cells are somewhat less efficient than monocrystalline cells, but are more efficient when the sun reaches low incidence angles on the solar cell.

**The thin film cell or amorphous silicon:**

It uses a new technology consisting of a thin film of pure silicon glass on a glass or ceramic substrate. This layer does not exceed 20 μm. The thickness of the entire cell is 300 to 800 μm. The substrate may also be plastic which allows the production of flexible modules.

Currently the efficiency of these cells is around 13% although in laboratories efficiency levels of 15% have been reached. The advantage of this technology is that it is much cheaper than the crystalline cells, it allows the formation of flexible modules and in the manufacturing process no polluting elements are used. They have a performance less than half that of crystalline type cells.

Typically for 12V Systems, 36 cells are connected in series in one PV module.




Figure 1 Types of solar cells

### Lifespan

In general, the PV modules are the longest-lasting component of the system, and the lifespan depends on its design, the environment and the operating conditions.

They are designed to withstand all weather conditions, including arctic cold, desert heat, tropical humidity, winds above 125 mph (200 km/h) and 25 mm hail at terminal speed.

Certain PV modules, such as thin film silicon types, suffer a predictable drop in performance during the first few months of operation, which decreases until it eventual cessation. Thereafter, the performance of the modules is relatively stable. In polycrystalline modules, this kind of degradation is much smaller.

Longer term degradation of around half percent a year can be expected. The overall life span of the PV module is likely to be limited by other factors rather than degradation of the silicon. A lifespan of 20 years or more can typically be expected.

### Current - Voltage Curve

The operation of a solar cell can be represented by a current - voltage curve (I-V) as in the figure 1. When the cell is not connected, an open circuit voltage is obtained Voc, and when the cell is shorted, the current Isc is obtained (under standard test conditions of 1000 W/m² solar irradiance, 25°C cell temperature, Air Mass 1.5).

For an increase in voltage from 0 to Voc the current is almost constant up to a voltage VMPP and from there it descends rapidly. As P = V x I at any point the power P can be calculated. What matters is to obtain the maximum power, i.e. when the area of the rectangle V x I is maximum. The Pmax point is also known as the maximum power point (MPP). The maximum power in Watts of the solar panel arises from multiplying IMPP by VMPP.




Figure 2 Current Voltage Curve

It can be observed that the maximum voltage (Voc) corresponds to the measurement without consumption, that is to say open circuit.

In contrast, the maximum current (Isc) is obtained by short-circuiting the positive and negative terminals of the solar panel.

The quality of a solar cell is determined by the relation between the area of the rectangle Voc x Isc and the area of the rectangle VMPP x IMPP and is known as a factor of quadrature (fill factor FF).

### Temperature Influence

Solar cells lose efficiency of voltage generated when their temperature increases. It is not surprising that a solar panel reaches temperatures in excess of 50ºC in summer, causing a reduction of the generated voltage of 15%.




Figure 3 Influence of temperature to efficiency of solar cells

The power of the solar modules is given under standard conditions of measurement, which is 1000 W/m² solar irradiance, 25°C cell temperature and Air Mass 1.5. The typical power output of a module is usually less than the output under standard conditions.

### Thermal Characteristics

Thermal characteristics are the most significant technical parameters to predict the future behaviour of the voltage in a solar module. The output current has low influence due to thermal changes. There are two important parameters:

* Nominal operating temperature of the cell (NOCT):

It is the temperature reached by the cells of the module under normal operating conditions, mainly at 20ºC of ambient temperature and irradiance of 800 Watt / m2. The NOCT has a direct relationship with the temperature reached by the cells at a given ambient temperature, and the lower the module temperature the better it will work and the more power it will deliver. Therefore the smaller the NOCT is better.

* Power temperature coefficient:

Indicates the percentage loss of solar module output power for each degree above 25°C which increases the temperature of the solar module. The smaller, is better.

### Solar Panel Orientation

Solar panels should be usually oriented toward the equator to maximise power output. The tilt angle should be chosen with regard to insolation, geographic location, self-cleaning capabilities, available space, etc.

In the case of floating aids it is not possible to guarantee the orientation of the modules, so a reduction factor must be applied.

It should also be taken into account that solar modules are sensitive to the presence of small shadows, even a narrow shadow can significantly decrease the output power. For example shadows generated by vegetation, buildings, daymarks and handrails can cause problems and should be avoided.

In some locations, fouling of the surface may be an issue. In these locations, it is recommended to avoid horizontal placement and that solar panels are installed with an inclination that promotes self-cleaning.




Figure 4 Power reduction approximately 90% due to shadow




Figure 5 Power reduction approximately 75% due to shadow

## General Information on Batteries

### Minimum and Maximum Capacity

The minimum battery capacity will depend on the choice made or imposed for the following design constraints:

* maximum daily depth of discharge;
* lowest acceptable level of charge during the winter months;
* allowance for 'no sun' days (from meteorological or insolation data). According to the inquiry, 20 days minimum is a rule of thumb for medium latitude (less in lower latitudes and more in higher ones);
* ease of access to the AtoN;
* ability of the battery to accept the peak output of the generator without overcharging, mainly for sealed batteries (a situation that may arise with a self-regulating system).

It should be noted that:

1. The maximum battery capacity will usually be determined by consideration of cost, available space, weight, and handling capacity. As a general rule the number of batteries in parallel should be kept to a minimum. (Five is a typical figure for good quality batteries coming from the same production batch, installed at the same time and working under the same regime of charge and discharge. It could vary according to the quality of the battery). Some manufacturers offer individual cells or blocks of 2 or 3 cells, with high capacity, and it is usually better to use these in series rather than to parallel smaller batteries.
2. Use of lead-acid batteries may require an increase in battery capacity to prevent deep discharge during winter months, but in this situation the effect of low temperature on the battery should be taken into account. For these reasons nickel-cadmium, nickel metal hydride and lithium ion batteries should be considered for the worst cases (very high latitude in the northern and southern hemispheres and very low temperature).
3. Batteries with low self–discharge become important when the design requires a long autonomous period for the system.

### Autonomy time

The battery is designed to supply energy under specified conditions for periods of time without or with minimum solar insolation. When calculating the required battery capacity, the following items should be considered:

* required daily / seasonal cycle (there may be restrictions on the maximum depth of discharge);
* time required to access the site;
* ageing;
* temperature impact;
* future expansion of the load;
* local weather conditions.

# INPUT DATA

In the process of designing a solar power system it is also important to be aware of some general safety factors. The following examples highlight issues to consider as you enter data into the solar sizing program.

To use the program, it is necessary to input information on local solar irradiation, technical details of the AtoN loads, and details of the particular types of solar modules and batteries that are planned to be used. These are described below.

The areas on the spreadsheet with a yellow background require input data. References in brackets (‘[ ]’) are to the cells in the spreadsheet in which the data must be entered.

When the cursor is placed on any of the red-edged boxes, information windows are displayed.

## Solar Irradiation and duration of night

Information on Solar irradiation and duration of night can be obtained from a solar atlas, from the local meteorological office or from various Internet sites. IALA provides further information on how to acquire that data from public sources in the internet at <http://www.iala-aism.org/products-projects/technical-area/calculation-working-tools/solar-sizing-tool>.

The data is entered in table ‘radiation & duration of night’. In that table many locations can be stored. Stored data can be easily used in the ‘simulation’ table with the scroll down button [H4] which will transfer

* name
* latitude
* longitude
* radiation data
* (if available) night hours

to the ‘simulation’ table. DAILY RADIATION [D#..O#] is entered in kWh/m² for each month of the year for the chosen mounting angle. In choosing minimum radiation data this is taking the worst-case-scenario. Information for angles of 0°, 30°, 60° and 90° are usually presented in a solar atlas.

In locations where solar irradiation is low, solar power systems may not be sufficient and other additional power sources may be required.

## Latitude and Longitude

The LATITUDE [B#] of the station in table ‘radiation & duration of night’ is entered as degrees North or South. If no duration of the night is given in [P#..AA#] the duration of the night will be calculated by the given latitude. Please be aware that this calculation is only an approximation which works in lower latitudes, but get less accurate in higher latitudes.

The LONGITUDE [C#] is used for description but could also be useful for deriving data from the internet.

## Orientation

A value must be entered in the ‘simulation’ table to account for ORIENTATION [B9] of the solar panels.

* if the panels are South facing in the Northern hemisphere (North facing in the Southern) this will be 1;
* if the panels are randomly orientated as would be the case on a floating AtoN, this will be 0.7.

## Voltage

The VOLTAGE [B6] must be entered in the ‘simulation’ table. This is the nominal design voltage for the power system and will usually be 12 volts, but in some cases may be 6 or 24 volts.

## Electrical Loads

The electrical loads that the system will support must be entered as lantern load for day- and night time and continuous load.

* Lantern Load;

LANTERN LOAD DAY [B10] and LANTERN LOAD NIGHT [F10] are the loads in Watts presented by the lantern (or other AtoN operating with a character) when it is switched on. The day load is only applicable if the lantern is in 24h use, e.g. a port entry light that is switched to a higher intensity during day time.

The proportion of the time that this load is switched on is described as the DUTY CYCLE [B11], which is entered as a percentage (e.g., 2sec on, 8sec off, would be a 20% duty cycle). Note: Switch closure time must be used rather than incandescent time.

* Continuous Load.

CONTINUOUS LOAD [B13] is the fixed or continuous load in Watts, presented by the flasher, charge regulator and any other fixed AtoN (racon, RTE, communications etc.).

## Switch Level

SWITCH LEVEL [B12] is entered as the time (in decimal hours) that the light switches on before dusk and switches off after dawn (e.g., 30 min. would be entered as 0.5 hour). Be aware that a light for 24h use could be switched to date time load with a negative number of switch level.

## Solar Panels

The parameters of the solar panels that you intend to use must be entered.

* Voltage

This is the voltage at maximum power point, entered at UMPP [B7] in volts. This value can be obtained from manufacturers data.

* Age

AGE [B5] is a measure of the reduction in the efficiency of the module during its working life (e.g., if the module degrades 1% each year of its working life and it will be used for 15 years then a figure of 15x1=15% will be entered). The manufacturer can provide some guidance on this.

* Power

The peak power of the total number of solar panels that you will use (the array) will be entered as POWER [B8] in watts. This will be a multiple of the peak power of the individual modules that you have chosen. Again, this information will be available from the manufacturer.

In practice, the size and number of the panels will depend on available space at the AtoN site and possibly by transport constraints. An initial estimate (guess) will have to be made of the number and hence peak power of the solar panels. This will then be refined by iterative use of the program.

## Batteries

Information regarding the batteries must be entered. A battery type must be chosen that will be suitable for the AtoN environment (e.g., spill-proof batteries for buoys, NiCd batteries may be considered for very low temperatures, battery dimensions will be limited on buoys, weight may be limited by local lifting facilities, transport systems, etc.).

* Maximum Useable Capacity

From manufacturer’s information and design guidelines, a value must be chosen for the MAXIMUM USEABLE CAPACITY [B15]. This is the percentage of the battery capacity that can safely be discharged without reducing the working life of the battery (e.g., 80%).

The maximum useable capacity may be adjusted dependent on the location of the system and the importance of the AtoN. The higher the significance of the AtoN the higher safety level (and lower maximum usable capacity) may be required.

The type of the battery and the manufacturer specifications have to be considered to realize the expected lifetime. Storage and loading conditions are essential for the durability of the battery.

* Efficiency

BATTERY EFFICIENCY [B16] is the recharge efficiency of the battery expressed as a ratio of the charge energy (input) to the energy delivered to the load (output). This is calculated as input over output. This figure can be obtained from the manufacturers.

The variation of temperature and the surrounding humidity will affect the lifespan of the battery. To sustain the safety and efficiency of the battery, good ventilation of the battery enclosure is required.

* Capacity

BATTERY CAPACITY [B14] is entered as Ah (Ampere hours) when the total battery bank is discharged over a 100-hour period. This will be a multiple of the capacity of the individual batteries. If an estimate (guess) is entered for the total battery capacity, then the program will calculate the number of days that the system will be able to work, without any solar gain, at the time of year when there is the minimum sunlight. It will also provide a graphical presentation of the solar system energy balance throughout the year.

**Please note:**

At ‘simulation’ table columns [S..U] are hidden. They include some auxiliary calculations only.

# OUTPUT DATA AND ITERATION

The DAYS WITHOUT GAIN [B17] provides a measure of the reserve capacity of the system. This may be referred to as the ‘No Sun Reserve’. Numbers of days may be chosen, depending on the local weather conditions for recharging the system during the winter period, or the distance to travel to the site for repairs if failure should occur. An adapted preventive maintenance is necessary.

The system design can then be refined by varying the numbers of solar panels (POWER [B8]) or batteries (BATTERY CAPACITY [B14]) to achieve a practical solution to provide the required number of DAYS WITHOUT GAIN [B17].

If the initial system design is incorrect and the proposed battery becomes fully discharged then an ‘error’ sign will appear in the DAYS WITHOUT GAIN [B17] and Ah [E21..F32] columns.

# END USER LICENSE AGREEMENT (EULA) FOR IALA SOFTWARE – IALA SOLAR SIZING PROGRAM

IMPORTANT – READ CAREFULLY: This End-user Licence Agreement (‘EULA’) is a legal agreement between you (either an individual or an organization) and IALA for the IALA software product identified above, which includes computer software and may include associated media, printed materials and ‘online’ or electronic documentation. By installing, copying, or otherwise using THE IALA SOLAR SIZING PROGRAM, you agree to be bound by the terms of this EULA. If you do not agree to the terms of this EULA, do not install or use the Program.

## Software product licence

The IALA Solar Sizing Program is licensed, not sold.

1. GRANT OF LICENCE.

This EULA grants you the right to install and use an unlimited number of copies of the IALA Solar Sizing Program.

1. REPRODUCTION AND DISTRIBUTION.

You may reproduce and distribute an unlimited number of copies of the IALA Solar Sizing Program; provided that each copy shall be a true and complete copy; including all copyright and trademark notices, and shall be accompanied by a copy of this EULA. Copies of the IALA Solar Sizing Program may be distributed as a standalone product or included with your own product.

1. COPYRIGHT.

All title and copyrights in and to the IALA Solar Sizing Program (including but not limited to any images, photographs, animations, video, audio, music, text, and ‘applets’ incorporated into the IALA Solar Sizing Program), the accompanying printed materials, and any copies of the IALA Solar Sizing program are owned by IALA or its suppliers. The IALA Solar Sizing Program is protected by copyright laws and international treaty provisions.

## Miscellaneous

Although IALA is an international, non-governmental organization, local national laws may apply to this EULA.

Should you have any questions concerning this EULA, or if you desire to contact IALA for any reason please contact IALA Secretariat, 10 rue des Gaudines, Saint Germain en Laye, 78100, France.

## Limited Warranty

1. NO WARRANTIES.

IALA expressly disclaims any warranty for the IALA Solar Sizing Program. The IALA Solar Sizing Program and any related documentation is provided ‘as is’ without warranty of any kind, either express or implied, including, without limitation, the implied warranties or merchantability, fitness for a particular purpose, or noninfringement. The entire risk arising out of use or performance of the IALA Solar Sizing Program remains with the user of the product.

1. NO LIABILITY FOR DAMAGES.

In no event shall IALA, or its suppliers be liable for any damages whatsoever (including, without limitation, damages for the loss of business profits, business interruption, loss of business information, or any other pecuniary loss) arising out of the use of or inability to use this IALA product, even if IALA has been advised of the possibility of such damages.

# ACRONYMS

Ah Ampere hours

AtoN Marine aid(s) to navigation

C100 Capacity at 100 hour discharge rate, Annex A

EULA End-user Licence Agreement

ISC Current at short circuit

IMPP Current at Maximum Power Point

kWh/m2 kilowatt hours per square metre

NiCd Nickel Cadmium (battery)

Pmax Maximum power

RTE Radar Target Enhancer

VOC Voltage at open circuit

VMPP, UMPP Voltage at Maximum Power Point, Annex A

W Watt

W/m2 Watts per square metre

Wpeak Watts peak

2. SAMPLE PAGE FROM THE SOLAR SIZING PROGRAM




Figure 6 Screenshot of the Excel workbook